## Slide 1: Sedimentation

## Slide 2: Topics
Introduction
Capture velocity
Plate settlers
Floc rollup
Entrance region
Floc blankets
Floc resuspension
Floc Hoppers
Delivering flocs
Minimum channel width
Scour velocity
Extras!

## Slide 3: Conventional Surface Water Treatment
Screening, grit removal, flow measurement
Mechanical Rapid Mix
Mechanical Flocculation
Sedimentation
Rapid Sand Dual
Media Filtration
Disinfection
Storage
Distribution
Raw water
Coagulant
Cl2
sludge
sludge
Backwash water

## Slide 4: AguaClara Surface Water Treatment
Screening, grit removal, flow measurement
Hydraulic
Flocculation
Plate Settlers
Stacked Rapid
Sand Filtration
Storage
Distribution
Raw water
Coagulant
Cl2
sludge
sludge
Backwash water
Floc Blanket
Floc Hopper

## Slide 5: AguaClara Sedimentation Tank
Dump poorly flocculated water channel
Exit Weir that controls water levels all the way upstream to the next free fall (LFOM!)
Notes: Exercise: Tell the story of the journey of a large floc, a small floc, a rouge loner clay particle, and of a water molecule as each travels through this sedimentation tank.
How do plate settlers work

## Slide 15: AguaClara Sed Tank Geometry

## Slide 16: Flocculation SWOT (strength, weakness opportunities, threat) for SWOT (safe water on tap)
Strength
  Rapidly reduces the primary particle concentration
  Produces flocs that can be captured by sedimentation or filtration
Weakness
  Always leaves a significant number of primary particles
  Further increases in expenditure of energy and reactor volume don’t produce significant improvement

## Slide 17: Flocculation is unable to aggregate all primary particles
Flocs are useless in flocculators
No successful collisions between primary particles and flocs

## Slide 18: Primary particle approaching floc in uniform shear* (edge of knowledge alert)
Thickness of viscous boundary layer, d, scales with floc diameter
Relative velocity goes to zero at best location for contact
Only similar sized particles can extend through each other’s viscous boundary layer.
Flat plate
Notes: I haven’t been able to find literature that demonstrates this effect.
Likely that the water contained within a floc simply rotates with the floc and that no new water enters the floc in a shear flow.

## Slide 19: Time to switch strategies
Shear is what we used to create collisions between particles and significantly reduce the concentration of primary particles
Shear PREVENTS particles of different sizes from colliding
We’d like to get collisions between big flocs and primary particles (We need relative motion and we can’t use shear!)
How else can we get relative motion?

## Slide 20: Primary particle approaching floc under influence of gravity in uniform velocity
No boundary layer at the floc stagnation point!
There exists a target where even small particles can reach the floc
Gravity holds the floc stationary

## Slide 21: Floc maximum size based on each hemisphere trying to rotate
Each half of the floc experiences drag that tends to cause that half of the floc to rotate
Buoyancy is at 3/8 r
Drag is at greater distance from center of sphere, but I don’t know how to calculate this.
Result is torque that puts bottom of sphere in tension.
Buoyancy
Drag
Notes: https://en.wikipedia.org/wiki/List_of_centroids
Centroid of hemisphere is at 3/8 r

## Slide 22: Floc blanket model
Floc blanket is a high concentration of flocs that are remaining relatively stationary in a uniform upward flow
The upward flow is carrying small particles with terminal velocities that are smaller than the upward velocity
Expect first order removal of small particles with respect to number of big flocs they pass by (depth of the floc blanket)

## Slide 23: Floc Blanket Research

## Slide 24
Flocculator
Sedimentation Tank
Tube Settlers
No filter….

## Slide 25
Notes: How does the floc blanket remove small particles?
Are plate settlers needed after a floc blanket?
What determines how fast the floc/water interface rises? 100mg/L*1mm/s = 3000 mg/L * x mm/s
Why might a floc blanket reduce settled water turbidity?
How is water entering the tank?
Where do the solids eventually go?
What mechanisms could result in particle aggregation in a floc blanket?
It’s a filter
It’s a flocculator
Wait, filters and flocculators are really quite similar. (particles colliding and attaching)
New question: which flocs are active and which flocs are inactive in the floc blanket?

## Slide 26
Turbidity stops decreasing before floc blanket stops growing!
Notes: How does the floc blanket remove small particles?
Are plate settlers needed after a floc blanket?
What determines how fast the floc/water interface rises? 100mg/L*1mm/s = 3000 mg/L * x mm/s
Why might a floc blanket reduce settled water turbidity?
How is water entering the tank?
Where do the solids eventually go?
What mechanisms could result in particle aggregation in a floc blanket?
It’s a filter
It’s a flocculator
Wait, filters and flocculators are really quite similar. (particles colliding and attaching)
New question: which flocs are active and which flocs are inactive in the floc blanket?

## Slide 27: Floc blanket observations
First order removal with respect to depth initially
Turbidity above the floc blanket is similar to raw water turbidity (Casey Garland observation)
Primary particle capture may continue at floc blanket depths greater than 1 m

## Slide 28: How do floc blankets form?
Flocculator flocs are captured by the plate settlers and they form larger flocs as they slide back into the floc blanket
The concentration of these larger flocs slowly increases and they begin colliding and attaching to each other in the floc blanket zone (or perhaps in the plate settlers!)
Once the flocs reach a size that has a settling velocity larger than the upflow velocity they converge at the bottom of the sed tank

## Slide 29: Floc blankets are very different from flocculation
Flocculation
Shear flow
Particles can only attach to similar sized particles
Primary particle aggregation rate slows
Effluent contains many small flocs and a few NTU of primary particles
Floc Blanket
Differential sedimentation
Only very small particles attach to floc blanket flocs
Flocculator flocs can’t attach to floc blanket flocs
Effluent contains many small flocs and (much?) less than 1 NTU of primary particles*
First order removal of primary particles with depth**
*need to measure!
**need a model!

## Slide 30: Flocculator flocs approaching floc blanket floc*
Floc blanket floc size is limited by fluid or floc-floc shear
The fluid drag force acting to keep an impinging floc moving increases with d
V increases rapidly with d in boundary layer
* Edge of knowledge
Floc blanket floc
Flocculator floc
Notes: This is why floc

## Slide 31: Previous state-of-the-art… SUPERPULSATOR® Clarifier
Suez environment
https://www.youtube.com/watch?v=UNhygQov69Q
Notes: https://www.youtube.com/watch?v=UNhygQov69Q
Why is pulsator needed?
Which end of the sed tank will have flocs rising rapidly? (two reasons)

## Slide 32: Pulsing flow in a floc blanket
What failed when they didn’t pulse?
What problem were they trying to solve?
Can we solve that problem a better way?
How long does it take for a superpulsator to build a floc blanket?
Notes: Sludge slowly buries more and more of the inlet manifold system.

## Slide 33: Sedimentation Tank Bottom Geometry determines if floc blanket builds
Flat bottom
Jet Reverser
Floc Hopper
Upflow velocity is 1 mm/s

## Slide 34: Floc Blanket Resuspender
Floc pickup location
Jet reverser
Diffuser tubes flattened to achieve line source
Flat bottom
Centered jet
Offset jet

## Slide 35: Cross section of an AguaClara sedimentation tank
Jet reverser
Sloped surfaces so that no sludge can accumulate
Plate settlers
Effluent manifold
Influent manifold
Plate settler modules that can be removed by an operator
Diffusers that create a line jet

## Slide 36: Prefabricated design (PF300)

## Slide 37: Floc Blanket Resuspender
Inlet diffuser
How does this animation violate the laws of physics?

## Slide 38: The jet reverser creates a vertical jet that resuspends settled flocs
All surfaces must transport particles to a resuspension zone.
Sludge produces gas that suspends particles.
Sedimentation tanks should have zero sludge!
May have application in other fluidized bed reactors.
7.5 cm
Notes: May have application in other fluidized bed reactors too! No patents – you can use this new technology

## Slide 39: Floc Blanket Resuspension
All surfaces in the sed tank with a horizontal component must return settled flocs to a resuspension zone
Floc resuspension geometry works by having a flocculated water jet with a high vertical velocity component that returns settled flocs to the floc blanket

## Slide 40: The jet deflects more when it has less momentum
8.9 mm Jet Diameter
3.9 mm Jet Diameter
Jet
Jet
Current of settled flocs
Current of settled flocs
<

## Slide 41: Floc blankets reduce settled water turbidity
Research required to determine optimal upflow velocity
Floc blanket formation requires
  All flocs be returned to the bottom of the sedimentation tank (plate settlers)
  All settled flocs must be resuspended by incoming water (jet reverser)
Floc blankets need flocculators AND plate settlers!

## Slide 42: Floc Blanket Questions
How deep should it be? (at least a meter???)
How do you design for flow rate variability?
Can a settled floc blanket be resuspended? (yes, at least sometimes)
What is the optimal velocity of the incoming jet? (high velocity is better for resuspension and breaks more flocs)
How will the operator observe the floc blanket? (flashlight through the plate settlers… Can we do better?)

## Slide 43: Floc Hopper Requirements
Control the depth of the floc blanket
Allow time for floc blanket overflow to concentrate (consolidate and dewater)
Floc blanket solids concentration decreases as coagulant dose increases (2 g/L is reasonable estimate)
Floc blanket flow into the floc hopper is a function of the mass flux of particles into the sed tank
We need to characterize the consolidation rate of the flocs to optimize the floc hopper design
Notes: If influent concentration is 20 mg/L, and floc blanket is 2000 mg/L, then what is the flow rate into the floc hopper

## Slide 44: Self-cleaning, sludge-free sedimentation tank (without using electricity)
Notes: Note that red dye can be removed by Polyaluminum chloride!

## Slide 45: Consolidation Questions
AguaClara built our first successful floc hoppers at Atima in Honduras. We have much to learn about this design. (and they work!!!!)
Floc consolidation in the floc hopper results in less water waste from the sedimentation tank.
Zero sludge sed tank design reduces need to clean sedimentation tank
We don’t yet have a method to guide the operation of the floc hopper. How will the operator know if the floc hopper valve should be opened further?

## Slide 46: Next unit process – Need to capture flocculator flocs that escape floc blanket
We currently use plate settlers because that is what everyone else uses.

## Slide 47: Sedimentation: Particle Terminal Fall Velocity
projected
Identify forces

## Slide 48: Drag Coefficient on a Sphere
laminar
turbulent
turbulent boundary
Stokes Law

## Slide 49: Floc Terminal Velocity
floc blanket velocity
Capture velocity for AguaClara plate settlers
Why flocculation is necessary!
The model takes into account the changing density of flocs
DFractal = 2.3 and d0 = 4 mm

## Slide 50: Horizontal Flow Sedimentation Tank
How much time is required for water to pass through the tank? _____
How far must a particle fall to reach the bottom of the tank (worst case)? _____
How fast must the particle fall?
H
W
L
entrance
exit
q
H
Settle Capture velocity: Property of the sedimentation tank. The slowest settling particle that the sedimentation tank captures reliably.
Will it remove any smaller particles? ___
Yes
Notes: How do I design a sed tank to capture 40 um flocs?

## Slide 51: Vertical Flow Sedimentation Tank
How much time is required for water to pass through the tank? _____
How far must a particle fall relative to the fluid to not be carried out the exit? _____
How fast must the particle fall (relative to the fluid)?
H
W
L
entrance
exit
q
H
Will any smaller colloids be captured? ______________________________ ______________________________
Only if they collide and grow so they have a sed velocity > vc

## Slide 52: Settle Capture Velocity Guidelines
Based on tube settlers
  0.12 – 0.36 mm/s
Based on Horizontal flow tanks
  0.24 to 0.72 mm/s
AguaClara adopted 0.12 mm/s in an effort to reduce effluent turbidity as much as possible because AguaClara wasn’t using filters
We’d like to know the performance curve. How does settled water turbidity change with the capture velocity? More research is needed!
Save plastic by increasing the capture velocity
Surface Water Treatment for Communities in Developing Countries. Christopher R. Schulz,Daniel A. Okun
https://www.brentwoodindustries.com/water-wastewater-products/tube-settlers/

## Slide 53: Vertical Flow Sedimentation Tanks
Have lower velocities and hence turbulence levels might be lower (plan view area is larger than width x height
Require careful attention to delivery and extraction of water
AguaClara uses channels at one end of the tanks that are connected to pipes to deliver and extract water – other geometries would be possible

## Slide 54: Stagnant Water (or Ripe for Innovation?)
State of the art in sedimentation…
  Empirical guidelines
  No understanding of scaling effects
Last significant paper on tube settlers was published in 1978
No significant revisions to Ten State Standards section on sedimentation in the past 30 years
extra
Notes: Personal communication with Daryl Bond and Frank Kulick of Brentwood Industries
9 records in Compendex for 1884-2010 Save Search - Create Alert -
((((tube settler) WN ALL)) AND ({water treatment} WN CV))
TUBULAR SETTLERS - A TECHNICAL REVIEW. Willis, Roderick M. Source: Journal / American Water Works Association, v 70, n 6, p 331-335, Jun 1978

## Slide 55: Sedimentation Tank Velocities
Notes: Give the two reasons why water accelerates when it enters the plate settlers.
It has less cross sectional area due to the space occupied by the plate settler material
It must maintained the same vertical flow velocity and it must also add a horizontal component due to the slope of the plates.

## Slide 56: 3 Steps to Sedimentation Success
The floc must be able to settle unto the surface of a plate or tube settler
  Settle capture velocity
It must slide down the incline to reach the lower section of the sedimentation tank
  Slide capture velocity
Finally the floc must be removed from the lower section of the sedimentation tank
  Floc hopper

## Slide 57: Plate Settler Redesign: Ideal plate settlers
Short retention time to reduce temperature density current effect (and reduce costs)
Ideally concentrate solids to points
4 strategies to prevent floc roll up
  Upflow with large plate spacing (conventional solution)
  Upflow with W plates that concentrate solids to density currents
  Fluid flow down (particles must be sucked out- venture in inlet diffusers)
  Fluid flow sideways
Notes: Perhaps it is time to redesign plate settlers!

## Slide 58: Critical path for capture
S
L
H
Critical path for capture
a
a

## Slide 59: Settle Capture Velocity for Plate (and Tube) Settlers
S
L
How far must particle settle to reach lower plate?
Path for critical particle?
Hc
What is total vertical distance that particle will travel?
H
What is net vertical velocity?
Particle velocity
a
a

## Slide 60: Compare Times
Time to travel distance Hc
Time to travel distance H
=
5 parameters… how do we choose?
Notes: The ratio of the upflow velocity to the capture velocity is really a measure of the reduction in tank area that is possible from using plate settlers. It is easy to get a factor of 10 reduction.

## Slide 61: Comparison with Q/As
a
S
L
a
Hc
H
Same answer!
As is horizontal area over which particles can settle
extra

## Slide 62: Equation for capture velocity
Tube settler

## Slide 63: Performance ratio (conventional to plate/tube settlers)
Compare the area on which a particle can be removed
Use a single plate settler to simplify the comparison
a
S
L
Conventional capture area
Plate/tube capture area
extra

## Slide 64: Settle Capture Velocity Confusion
Surface Water Treatment for Communities in Developing Countries, Schulz and Okun (1984)
Water Quality and Treatment (1999)
Weber-Shirk
Assume that the geometry is
Consistent, but no one uses this geometry except in labs
inconsistent
extra

## Slide 65: Thick Plate Settlers
a
S
L
a
hc
h
S Distance between plate settlers
B Center to center distance
T Plate settler thickness
Vertical velocity component beneath the plate settlers
Vertical velocity component between the plate settlers
extra

## Slide 66: Thick Plate Settlers
Mass Conservation
Geometry
extra

## Slide 67: Plate Settler Design (AguaClara approach)
Upflow velocity (determines size of tanks) (1 mm/s)
  If floc blanket is a goal then needs to be approximately 1 mm/s*
Capture velocity (0.12 mm/s)
  target turbidity
  particle size distribution after floc blanket
Plate angle (60 deg)
  self cleaning (60 deg works well)
Spacing (2.5 cm)
  Clogging (not a problem at 2.5 cm)
  floc roll up: Will the floc slide down? (next topic in the notes!)
Length of the plate settlers
  will be the parameter that we calculate
2011 AguaClara design
Needs research!
* Active research topic!

## Slide 68: Plate Settler Spacing Constraints: Floc Rollup
Why do we care? – What is the connection to sustainability?
Why not use the standard design?

## Slide 69: Floc Roll Up Solution Scheme: Another failure mode
Find the velocity gradient next to the plate
Find the fluid velocity at the center of the floc
Find the terminal velocity of the floc down the plate (for the case of zero velocity fluid)
Set those two velocities equal for the critical case of no movement
Find the floc sedimentation velocity that can be captured given a plate spacing (VSlide)
a
gsin(a)
g
a
a

## Slide 70: Infinite Horizontal Plates: Boundary Conditions
negative
No slip condition
u = 0 at y = 0 and y = S
S
y
t
let
be___________
u
What can we learn about t?
x
extra

## Slide 71: Navier Stokes Flow between Plates
is average velocity between plates
We have velocity gradient as a function of average velocity
Integrate to get average velocity
extra
Notes: q is flow per unit width
u is fluid velocity as a function of location
S is spacing between the plates

## Slide 72: Laminar Flow through Circular Tubes: Equations no gravity
Max velocity when r = 0
Velocity distribution is paraboloid of revolution therefore _____________ _____________
average velocity (V) is 1/2 vmax
R is radius of the tube
extra

## Slide 73: Velocity gradient at the wall
Where dp/dx is the pressure gradient in the direction of flow NOT due to changes in elevation
Plate geometry
extra
Tube geometry
Average velocity

## Slide 74: Floc Rollup Constraint
a
Linearized (plates)
gsin(a)
g
a
Velocity at center of floc
Failure point (floc stationary)
floc diameter
Terminal velocity
extra
a
Notes: d is floc diameter
What happens when floc slides down to high shear zone?

## Slide 75: Spacing as a function of floc terminal velocity
Sedimentation velocity solved for diameter
But terminal velocity and floc diameter are related!
This is the smallest spacing that will allow a floc with a given settling velocity to remain stationary on the slope (and not be carried upward)
extra

## Slide 76: Minimum Plate Settler Spacing (function of Floc Vt)
Plate settler spacing of 5 mm or larger should be adequate if the capture velocity is 0.12 mm/s
Fewer, but longer plate settlers due to higher upflow velocity in the sed tank
Current AguaClara design for
What happens if a floc forms from organic matter rather than clay?
Which flocs (big or little) are more like to slide up?
Notes: If we use a spacing that is smaller than this plot, then particles that reliably make it to the plate end up not being removed because the are rolled out the top! This is the minimum spacing that will not cause a reduction in performance.
Note that as Vt goes up, that S decreases. This means that larger flocs slide down more easily.
This is the minimum spacing to be able to capture particle with a sedimentation velocity of Vt. At smaller spacings flocs with a sedimentation velocity of Vt will roll up.
Is there a clearer way to plot this or some non dimensional way to show these results to make design easier?
How will this information be used in a design process?
First given the Vupplate and the target capture velocity we can find a minumum S.
Then given an actual design S we can use the capture velocity equation to get a plate length.
Or… It doesn’t work to use the ratio of Vt/VupPlate because Vt is also in the other term in the equation.

## Slide 77: Slide Capture Velocity
is the terminal sedimentation velocity (Vt) of the slowest-settling floc that can slide down an incline. Flocs with this terminal velocity (the slide velocity) will be held stationary on the incline because of a balance between gravitational forces and fluid drag. Flocs with a terminal velocity lower than will be carried out the top of the tube (i.e., “roll up”) even if they settle onto the tube wall. Thus, the slide terminal velocity represents a constraint on the ability of plate settlers to capture flocs.
What happens if the primary particles are less dense? _____
↑
extra

## Slide 78: Experimental Evidence that the Slide Capture Velocity Matters
All experiments were performed at the same settle capture velocity
Floc Roll-up and its Implications for the Spacing of Inclined Settlers Matthew W. Hurst, Michael J. Adelman, Monroe L. Weber-Shirk, Tanya S. Cabrito, Cosme Somogyi, and Leonard W. Lion. Journal of Environmental Engineering, submitted (2012)
If VSlide is bigger than VSettle, then some flocs that we expected to capture will slide out the top
extra
Notes: Floc Roll-up and its Implications for the Spacing of Inclined Settlers Matthew W. Hurst, Michael J. Adelman, Monroe L. Weber-Shirk, \\Tanya S. Cabrito, Cosme Somogyi, and Leonard W. Lion. Journal of Environmental Engineering, submitted (2012)

## Slide 79: Plate Settler Spacing effects
Plate settler spacing has a strong influence on sedimentation tank depth
Diminishing effect for small S
Reduced spacing results in increased pressure drop through plate settlers*
Which plate settlers will have more uniform flow distribution? ___________
Small S
*proof coming up…
1 cm spacing = 1.64 m deep
2.5 cm spacing = 1.84 m deep
5 cm spacing = 2.27 m deep
Notes: 6 L/s plant with 2 sed tanks.
I think that going to 1 cm spacing has promise for cutting plant costs. It would allow us to use deeper floc blankets. I wonder if we can devise a fabrication method that includes flow resistance on each plate.

## Slide 80: Pressure drop (from head loss) through plate settlers
Force balance
Viscous shear
Change L to maintain capture velocity
Velocity
Shear (wall on fluid)
Notes: The shear is acting on both plates. The pressure drop is due to the shear on the plates. The areas over which the shear and pressure act are different. As the space between the plates decreases the area over which the pressure is acting decreases too. Thus the pressure increases for two reasons. Area decreases and shear increases.

## Slide 81: Plate Settler Head Loss
Head loss is tiny! We need some head loss to get reasonable flow distribution between (and within) plates. This lack of head loss may be one of the reasons for poor performance of full scale plate settlers. The velocity of any turbulent eddies or mean flow needs to be less than ______ to achieve uniform flow through plate settlers. The floc blanket will end up helping us here!
4 mm/s
This represents an opportunity to improve design!
Notes: This sets the maximum velocity in the space above the plates settlers.
The lack of significant head loss through plate settlers means that any turbulence or mean velocities in the bottom of the sed tank will propagate through the plate settlers and result in non uniform distribution of flow between plates. In order to obtain reasonable uniform flow we need the velocities below the plate settlers to be close to 1 mm/s even if we use closely spaced plates. This is a daunting challenge given that the upflow velocity is 1 mm/s and given that the velocity coming from the inlet manifold ports is on the order of 100 mm/s (and thus turbulent eddies with velocities that are order 10 mm/s). The distance between the manifold ports and the bottom of the plate settlers will result in significant energy dissipation. The fact that AguaClara sed tanks are shallower than conventional design means that we need to understand and perhaps take additional steps to minimize velocities at the inlets of the plate settlers.
The AguaClara team is working to reduce velocities in the bottom of the sed tank by improving the design of the inlet manifold. The team is also evaluating the performance of small diameter tube settlers to confirm that there aren’t any other unforeseen problems caused by reducing the separation between the plate settlers.

## Slide 82: Plate Settler Conclusions…
Laminar flow
Parabolic velocity profile is established
Very low head loss (and thus flow distribution between plates is difficult to ensure)
Designed to capture flocs with sedimentation velocities greater than the settle capture velocity
Spacing determines the ability of the flocs to roll down the incline (slide capture velocity)

## Slide 83: Plate Settler Confusions…
We need a basis for choosing a settle capture velocity based on overall plant performance*
Smaller spacings have diminishing returns in terms of sedimentation tank depth. So for now we are using 2.5 cm.
Flocs made from natural organic matter may be less dense, more prone to floc rollup, and require larger spacing between plate settlers
* Predictive performance model for hydraulic flocculator design with polyaluminum chloride and aluminum sulfate coagulants. Karen A. Swetland, Monroe l. Weber-Shirk, and Leonard W. Lion. Journal of Environmental Engineering, submitted (2012)

## Slide 84: Floc Volcanoes
Intermittent floc volcanoes in the sedimentation tanks at San Nicolas
Flocs rise preferentially on one side of the sed tanks
Raw water turbidity = 4 NTU
PACl dose = 3.5 mg/L
Settled water turbidity varies between 0.5 and 4 NTU
Brainstorm! What is happening? Why does our plant do so poorly?
Notes: What do you know?
What could cause what is observed?
Which of those causes is consistent with observations?

## Slide 85: Settled Turbidity at San Nicolas
Turbidity (NTU)
Raw water
Settled water

## Slide 86: Plate Settler Problems: Temperature Gradients
Warmer water is less dense
Warm water rises
Cold water drops
Performance drops
Need a solution!
Could we further reduce residence time in sed tank so that density gradients are less significant?

## Slide 87: Lab scale floc blanket, tube settler, floc hopper

## Slide 88: Design of the Inlet Diffuser
If a sedimentation tank has a length of 6 m, a width of 1 m, a depth of 2 m, an upflow velocity of 1 mm/s, and a diffuser spacing () of 5 cm…
What is the port flow rate? ________________________
(50 mm)(1 m)(1 mm/s) = 50 mL/s

## Slide 89: Diffuser Slot Width
Proposed constraint is head loss in jet leaving the jet reverser (perhaps 1 cm)
Minimum width to not exceed target head loss
This head loss will improve flow distribution between diffusers
Notes: Note: No vena contracta here because the flow isn’t confined and thus there is no way for potential energy to turn into kinetic energy. Thus the jet can’t accelerate (contract) as it goes around the jet reverser.

## Slide 90: Is there a Vena Contracta?
Vena contracta is associated with a change in pressure that causes an acceleration of the fluid
The change in pressure is supported by an enclosed flow space and flow
What is the energy of the water leaving the diffuser pipe?
Prove that the flow can’t contract!
Notes: Pressure across parallel streamlines is constant. Take ascending jet at same elevation as exit from slot. Potential energy is the same. Pressure is the same. If flow accelerated it would require the pressure to drop in the jet, but the jet is always exposed to the open tank on the inner side of the jet and thus the pressure can’t be dropping along the jet.

## Slide 91: Diffuser Width
is about 380 mm/s!
Compare jet velocity with head loss through plate settlers. The momentum of this jet must be attenuated through jet expansion and floc blanket.
Round up to 1/8” mold

## Slide 92: Sed Tank Inlet design Post 2014
Floc break up is likely not a constraint for delivery of water to the sedimentation tanks.
Flow distribution and the ability to resuspend a settled floc blanket are likely the most important constraints
Floc hopper needs design algorithms (highlighted by design of 1 L/s plant)

## Slide 93: Design Review
Comparing designs
  Pan-American Health Organization (CEPIS)
  Superpulsator®
  AguaClara
What is good?
What can be improved?
What could (or did) fail?

## Slide 94: Santa Rosa de Copan: CEPIS Plant Tour

## Slide 95: CEPIS/OPS designs – Vertical Flow
Critique this design
Sludge will accumulate on the flat tank bottom
How are plate settlers suspended?
Inaccessible channels

## Slide 96: CEPIS Sed
Plate settlers and effluent launders
Launders must be perfectly level using this system
Submerged launders are better

## Slide 97: AguaClara Evolution
Ojojona - Vertical Flow Sedimentation (2 m)
Tamara and Marcala - sloped bottoms of the tanks (2 m)
4 Comunidades - Inlet manifold below the sloped bottoms (1.55 m) and no elevated platforms
Agalteca – Inlet manifold pipe with orifices

## Slide 98: Cuatro Comunidades

## Slide 99: Cuatro Comunidades Sludge
Notes: Mud in the bottom of the sed tank in 4 Com in May during the first cleaning. Note as Monroe inferred that there doesn’t seem to bee too much depth of accumulation in the middle of the tank; there seems to be more behind the panels that form the triangle. Note that the mud behind the panels is dark underneath (and reeks) meaning that there is some kind of biological decay occurring. That mud is very tough and doesn’t come out with just wash water, as you see in the next picture, a shovel is necessary. I think some kind of tool will always be needed to clean any plant, but the easier the mud can come out the better off for operation and water quality.

## Slide 100: Brainstorm
Why is this problem occurring?
How would you fix this problem?
What concepts might be important in obtaining a solution?
What are some of the other constraints that must be considered?

## Slide 101: Large scale circulation and poor performance

## Slide 102: Floc escape at Agalteca (2009)

## Slide 103: Flow Straightening Tubes to Eliminate Circulation
Notes: This was tested at multiple plants and is much better than the manifolds that were simple pipes with a row of holes!

## Slide 104
No floc blanket in this design because of flat bottom section that covers the drain

## Slide 105: Moroceli – Fall 2014

## Slide 108
Holes to drain beneath jet reverser were eliminated beginning in 2015.
Jet reverser
Diffusers
Inlet Manifold

## Slide 109
Inlet manifold/drain
Slot that runs the length of the sed tank
Sed tank cross- section showing bottom geometry
1 m
Identify the failure modes for this geometry
Notes: Flocs go down hill the whole way to the sed tank. Then they are resuspended until they land in the floc hopper and then it is down hill again to the plant drain.
There is only one place in the sed tank where flocs are resuspended.

## Slide 110: Inlet Manifold Improvements at Tamara
Chart: Cumulative Percentage of the Samples

## Slide 111: How can you drain and then refill a sedimentation tank?
Notes: Why does the plug have a vertical tube? Serves as a handle and an air vent.

## Slide 112: Questions
Why do horizontal flow sedimentation tanks perform much worse than theory predicts? (eliminate inlet manifold?)
Why do we use plate settlers?
What is the failure mechanism for plate settlers for small spacing?
What helps the flow divide evenly between the sed tanks? (hint… flow resistance)
Notes: 6m / 0.17m/s
4mm/s
Entrance channel design is now governed by flow distribution constraint. Don’t drop the flocs, distribute the water between sed tanks.

## Slide 113: Sedimentation Conclusions
3 processes in one tank: flocculation, sedimentation, consolidation
Eliminate the need for mechanized sludge removal by using hydraulic sludge removal
Provide the operator with options for dumping poorly treated water
Make the sedimentation tank easy to operate and maintain

## Slide 114: Sedimentation Conclusions
Plate settlers make it possible to significantly reduce sedimentation tank area
Reduced plate spacing for shallower tanks
Floc blankets improve performance and provide a method to remove sludge
Flow distribution is VERY important
Hydraulic residence time of 24 minutes is sufficient for efficient sedimentation

## Slide 115: More sedimentation tank failure modes
Buoyant flocs
  Anaerobic sludge
  Dissolved air flotation from compressed air in the transmission line or from increased temperature
Collapsing floc blankets from bad bottom geometry
Floc volcanoes from temperature increases
Curtains on windows to block sunlight
Slime from iron oxidizing bacteria

## Slide 116: Density of the floc blanket
Density of the floc blanket is approximately equal to the mass of clay and water divided by the volume
Water volume fraction
Neglecting PACl
Empirical equation

## Slide 117: Flocculation in a floc blanket due to shear from suspended flocs
See filtration notes for derivation
Head loss in a fluidized bed
is approximately = 1 and is a function of CClay
Density of fluidized bed
Porosity of floc blanket

## Slide 118: Fluidized flocs provide a collision potential of a few thousand
Assuming: 1 mm/s upflow velocity, 1000s residence time
How does a small Gq cause a large reduction in turbidity?
Low G: flocs grow larger
Notes: Clearly, adding this much Gtheta to the flocculator would not have helped so much. So there is something else going on here.
Perhaps it is because it is at a much lower G and thus there is an opportunity for all flocs to grow again.
Tapered flocculation?
The high concentration of flocs provides many opportunities for clay particles to collide with big flocs. But are those collisions successful? Unknown.