## Slide 1: Self-Cleaning Floc Filter Settler

## Slide 2: Topics
Introduction
Floc-filter/Sed
Floc filter
Floc resuspension
Floc Hoppers
Capture velocity
Plate settlers
Floc rollup

## Slide 3: Conventional Surface Water Treatment
Screening, grit removal, flow measurement
Mechanical Rapid Mix
Mechanical Flocculation
Sedimentation
Rapid Sand Dual
Media Filtration
Disinfection
Storage
Distribution
Raw water
Coagulant
Cl2
sludge
sludge
Backwash water

## Slide 4: AguaClara Surface Water Treatment
Screening, grit removal, flow measurement
Hydraulic
Flocculation
Plate Settlers
Stacked Rapid
Sand Filtration
Storage
Distribution
Raw water
Coagulant
Cl2
sludge
sludge
Backwash water
Floc Filter
Floc Hopper
Backwash recycle proposed

## Slide 5: Floc-filter/Sed
Dump poorly flocculated water channel
Exit Weir that controls water levels all the way upstream to the next free fall (LFOM!)
To filters
floc filter
Notes: Exercise: Tell the story of the journey of a large floc, a small floc, a rouge loner clay particle, and of a water molecule as each travels through this Floc-filter/Sed.
How do plate settlers work

## Slide 6: Elements of the Floc-filter/Sed
Jet reverser
Sloped surfaces so that no sludge can accumulate
Plate settlers
Effluent manifold
Influent manifold
Plate settler modules that can be removed by an operator
Diffusers that create a line jet

## Slide 7: Floc-filter/Sed
How do the flocs get into the floc hopper?
What controls the water level?
How could the operator see what is in the floc hopper?
Top view of channels
End view
floc hopper
Plate settlers
floc filter

## Slide 9: We need your help to Name the Floc-filter/Sed!
We’d like a name that describes what it does
Self-cleaning with floc filter and plate settlers
Much more than a sedimentation tank
I’m calling it a Floc-filter/Sed in these notes temporarily

## Slide 17: Flocculation SWOT (strength, weakness opportunities, threat) for SWOT (safe water on tap)
Strength
  Rapidly reduces the primary particle concentration
  Produces flocs that can be captured by sedimentation or filtration
Weakness
  Always leaves a significant number of primary particles
  Further increases in expenditure of energy and flocculator volume don’t produce significant improvement

## Slide 18: Flocculation is unable to aggregate all primary particles
Flocs are useless in flocculators
No successful collisions between primary particles and flocs
Notes: I haven’t been able to find literature that demonstrates this effect.
Likely that the water contained within a floc simply rotates with the floc and that no new water enters the floc in a shear flow.

## Slide 19: Four sizes/types of Floc
New flocs in the floc filter
Full flocs in the floc filter
Primary particles and flocs too small to be captured by the plate settlers
Flocs that settle fast enough to be captured by the plate settlers but not fast enough to stay in the floc filter

## Slide 20: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Inlet (from flocculator)
Floc Hopper
Floc Filter
Effluent manifold
Plate Settlers
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 21: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Flocs are filters!
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 22: Flocs have a finite capacity to capture incoming particles
The fraction of the projected area flow that enters the floc, , is a function of the floc porosity (or fractal dimension)
No boundary layer preventing particles from entering the floc!
We are trying to figure out how to
  Preferentially waste flocs that are full
  Increase the concentration of flocs that have a low fractal dimension
I’m getting full
I’m stuffed (my fractal dimension is too big)

## Slide 23: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Flocs aggregate as they slide down the plate!
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 24: Flocs tumble down the plate settlers and grow larger
This creates the large flocs that can settle fast enough to stay in the floc filter from the flocs created by the flocculator
As big flocs fall from the plate settlers they break if they are bigger than the size set by the bond strength and gravity

## Slide 25: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Flocs in free fall have a maximum size!
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 26: Floc maximum size based on each hemisphere trying to rotate
Each half of the floc experiences drag that tends to cause that half of the floc to rotate
Buoyancy is at 3/8 r
Drag is at greater distance from center of sphere.
Result is torque that puts lower floc bond in tension.
Buoyancy
Drag
Notes: https://en.wikipedia.org/wiki/List_of_centroids
Centroid of hemisphere is at 3/8 r

## Slide 27: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Plate settlers capture flocs that settle faster than a velocity that we will calculate next!
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 28: Key ideas for Floc-filter/Plate Settlers
In floc filters small particles flow through large flocs (held in place by gravity) where they can collide with small particles
The maximum size of flocs in the floc filter is set by gravity
Plate settlers will capture particles that settle faster than the capture velocity of the settlers and grow them!
Notes: How do we know charge neutralization doesn’t explain flocculation
Floc aggregation begins even with very small dosages of coagulant long before the surface charge is neutralized
No transition in flocculation performance as the coagulant dose is gradually varied over a very wide range
No evidence of charge reversal causing deterioration in performance
A single physics-based model describes the full range of flocculation from low to high coagulant dosages
Coagulant nanoparticles are so large that they easily extend through the double layer and hence can directly bridge between two negatively charged particles
No one has been able to develop equations describing the role of charge neutralization
Confusion in the literature about whether WTPs use charge neutralization or sweep floc. No quantification of how you would know which hypothesized mechanism is operative

## Slide 29: We need an animation illustrating the Floc-filter/Sed
Steady state
Show view similar to sed tank slice we use for research
Concepts
  Full size Flocculator flocs go to plate settlers, slide, combine breakup from gravity and settle in the floc filter
  Tiny flocs travel up through floc filter and at some point go into a floc where they attach
  Excess flocs go to the floc hopper. Not sure if we should show the weir or a chimney

## Slide 30: Floc Filtration Ideas
Floc filter is a high concentration of flocs that are remaining relatively stationary in a uniform upward flow
The upward flow is carrying small particles with terminal velocities that are smaller than the upward velocity
Some fraction of the flow goes right through the flocs where they can collide and attach to particles inside the floc
The flocs in the floc filter have finite capacity for capturing incoming particles

## Slide 31: floc filter Research

## Slide 32
Flocculator
floc filter
Tube Settlers
No sand filter….

## Slide 33
Notes: https://www.youtube.com/watch?v=pytXC-1zWhw
<iframe width="590" height="483" src="https://www.youtube.com/embed/pytXC-1zWhw" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>
<iframe width="791" height="445" src="https://www.youtube.com/embed/pytXC-1zWhw?autoplay=1&start=285&end=360" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>
How does the floc filter remove small particles?
Are plate settlers needed after a floc filter?
What determines how fast the floc/water interface rises? 100mg/L*1mm/s = 3000 mg/L * x mm/s
Why might a floc filter reduce settled water turbidity?
How is water entering the tank?
Where do the solids eventually go?
What mechanisms could result in particle aggregation in a floc filter?

## Slide 34: How do floc filters form?
Flocculator flocs are captured by the plate settlers and they form larger flocs as they slide back into the floc filter
The concentration of these larger flocs slowly increases and they begin colliding and attaching to each other in the floc filter zone (or perhaps in the plate settlers!)
Once the flocs reach a size that has a settling velocity larger than the upflow velocity they converge at the bottom of the sed tank

## Slide 35: Floc filters are very different from flocculation
Flocculation
Shear flow
Particles can only attach to similar sized particles
Primary particle aggregation rate slows
Effluent contains many small flocs and a few NTU (or mg/L) of primary particles that haven’t been flocculated
Floc filter
Filtration inside flocs
Only very small particles flow into the floc filter flocs and then attach inside the floc
Full size flocculator flocs can’t attach to floc filter flocs (shear on outside of floc filter flocs is too high)
The suspension leaving the top of the floc filter contains small flocs from the flocculator as well as some primary particles

## Slide 36: Sedimentation Tank Bottom Geometry determines if floc filter builds
Flat bottom
Jet Reverser
Floc Hopper
Upflow velocity is 1 mm/s

## Slide 37: floc filter Resuspender
Floc pickup location
Jet reverser
Diffuser tubes flattened to achieve a continuous jet of water the entire length of the Floc-filter/Sed
Flat bottom
Centered jet
Offset jet

## Slide 38: floc filter Resuspender
Inlet diffuser
How does this animation violate the laws of physics?

## Slide 39: The jet reverser creates a vertical jet that resuspends settled flocs
7.5 cm
All surfaces must transport particles to a resuspension zone.
Sludge produces gas that suspends particles.
Sedimentation tanks should have zero sludge!
May have application in other fluidized bed reactors.
Notes: May have application in other fluidized bed reactors too! No patents – you can use this new technology
<iframe width="640" height="360" src="https://www.youtube.com/embed/oHcKJD_OdfI?autoplay=1&mute=1&start=388&end=398&showinfo=0&rel=0" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>

## Slide 40: The jet deflects more when it has less momentum
Failure occurs below jet velocity of 75 mm/s
8.9 mm Jet Diameter
3.9 mm Jet Diameter
Jet
Jet
Current of settled flocs
Current of settled flocs
<

## Slide 41: Floc filter Questions
How do you design for flow rate variability?
Can a settled floc filter be resuspended? (yes, at least sometimes)
What is the optimal velocity of the incoming jet? (> 75 mm/s and such that G in the jet is low enough )
How will the operator observe the floc filter? (flashlight through the plate settlers… Can we do better?)
How could we make it work better?

## Slide 42: Self-cleaning, sludge-free Floc-filter/Sed (without using electricity)
Notes: Note that red dye can be removed by Polyaluminum chloride!

## Slide 43: Floc Hopper Requirements
Weir controls the depth of the floc filter
Floc filter flow into the floc hopper is a function of the mass flux of particles into the sed tank
Flocs in the floc filter settle at a rate equal to the upflow velocity (1 mm/s)
The area required for consolidation could be based on max raw water turbidity and the corresponding floc filter concentration
  More work needed for a model for the floc filter concentration
Notes: If influent concentration is 20 mg/L, and floc filter is 2000 mg/L, then what is the flow rate into the floc hopper

## Slide 44: Previous state-of-the-art… SUPERPULSATOR® Clarifier
Notes: https://www.youtube.com/watch?v=UNhygQov69Q
Why is pulsator needed?
Which end of the sed tank will have flocs rising rapidly? (two reasons)
<iframe width="640" height="360" src="https://www.youtube.com/embed/UNhygQov69Q?autoplay=1&mute=1&start=68&stop=214" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>

## Slide 45: Why is there pulsing flow in a SuperPulsator?
What failed when they didn’t pulse?
What problem were they trying to solve?
Can we solve that problem a better way?
Will sludge accumulate and go anaerobic?
Notes: Sludge slowly buries more and more of the inlet manifold system.

## Slide 46: Sedimentation!
How do we design a tank so that particles are separated from the water?
We will begin by looking at how simple sedimentation tanks (big rectangular or cylindrical open tanks) are supposed to work
Then we will explore plate settlers

## Slide 47: Horizontal Flow Sedimentation Tank
How much time is required for water to pass through the tank? _____
How far must a particle fall to reach the bottom of the tank (worst case)? _____
How fast must the particle fall?
H
W
L
entrance
exit
q
H
Settle Capture velocity: Property of the sedimentation tank. The slowest settling particle that the sedimentation tank captures reliably.
Will it remove any smaller particles? ___
Yes
Notes: How do I design a sed tank to capture 40 um flocs?

## Slide 48: Vertical Flow Sedimentation Tank
How much time is required for water to pass through the tank? _____
How far must a particle fall relative to the fluid to not be carried out the exit? _____
How fast must the particle fall (relative to the fluid)?
H
W
L
entrance
exit
q
H
Will any smaller particles be captured? ______________________________ ______________________________
Only if they collide and grow so they have a terminal velocity > vc

## Slide 49: Settle Capture Velocity Guidelines
Based on tube settlers
  0.12 – 0.36 mm/s
Based on Horizontal flow tanks
  0.24 to 0.72 mm/s
AguaClara adopted 0.12 mm/s in an effort to reduce effluent turbidity as much as possible because AguaClara wasn’t using filters
Now we have the connection between temperature, velocity gradient in the flocculator and jet reverser, and the plate settler capture velocity
Surface Water Treatment for Communities in Developing Countries. Christopher R. Schulz,Daniel A. Okun
https://www.brentwoodindustries.com/water-wastewater-products/tube-settlers/

## Slide 50: 3 Requirements for Plate Settler Success
The floc must be able to settle to the surface of a plate or tube settler
  Settle capture velocity
It must NOT slide or roll up the incline
  Slide capture velocity
It must roll down the plate and combine with other flocs to increase its terminal velocity so it can fall back into the floc filter (and become a contributing member of the floc filter)

## Slide 51: Critical path for capture
S
L
H
Critical path for capture
a
a

## Slide 53: Settle Capture Velocity for Plate (and Tube) Settlers
S
L
How far must particle settle to reach lower plate?
Path for critical particle?
Hc
What is total vertical distance that particle will travel?
H
What is net vertical velocity?
Particle velocity
a
a

## Slide 54: Compare Times
Time to travel distance Hc
Time to travel distance H
=
This ratio represents the plan view area reduction factor!
Notes: The ratio of the upflow velocity to the capture velocity is really a measure of the reduction in tank area that is possible from using plate settlers. It is easy to get a factor of 10 reduction.

## Slide 55: Plate Settler Design (AguaClara approach)
Upflow velocity (determines size of tanks) (1 mm/s)
  If floc filter is a goal then needs to be approximately 1 mm/s
Capture velocity (0.12 mm/s)
  Must capture the large flocs produced by the flocculator (and jet reverser)
Plate angle (60 deg)
  self cleaning (60 deg works well)
Spacing (2.5 cm)
  Clogging (not a problem at 2.5 cm)
  floc roll up: Will the floc slide down? (next topic in the notes!)
Length of the plate settlers
  will be the parameter that we calculate

## Slide 56: Plate Settler Spacing Constraints: Floc Rollup
Why do we care? – What is the connection to sustainability?
Why not use the standard design?

## Slide 57: Floc Roll Up Solution Scheme: Another failure mode
Find the velocity gradient next to the plate
Find the fluid velocity at the center of the floc
Find the terminal velocity of the floc down the plate (for the case of zero velocity fluid)
Set those two velocities equal for the critical case of no movement
a
gsin(a)
g
a
a

## Slide 58: Minimum Plate Settler Spacing
Assume fractal dimension of 2
Given that AguaClara uses a lower upflow velocity, , than many plate settler designs it is okay to use more closely spaced plates, S.
This failure mode will show up only with very low density core particles and cold water
Notes: plateAN = 60 * u.deg
vz = 1.2 * u.mm/u.s

## Slide 59: Plate Settler Spacing effects
Plate settler spacing has a strong influence on sedimentation tank depth
Diminishing effect for small S
Maintaining spacing becomes more challenging for small S because the plates are quite flexible
Too small an S will fail!
5 cm
2.5 cm
1 cm
Notes: 6 L/s plant with 2 sed tanks.
I think that going to 1 cm spacing has promise for cutting plant costs. It would allow us to use deeper floc filters. I wonder if we can devise a fabrication method that includes flow resistance on each plate.

## Slide 60: Plate Settler Conclusions…
Designed to capture flocs with sedimentation velocities greater than the settle capture velocity
Spacing determines the ability of the flocs to roll down the incline (slide capture velocity)

## Slide 61: Plate Settler Confusions…
We need a basis for choosing a settle capture velocity based on overall plant performance*
Smaller spacings have diminishing returns in terms of sedimentation tank depth. So for now we are using 2.5 cm.
Flocs made from natural organic matter may be less dense, more prone to floc rollup, and require larger spacing between plate settlers
* Predictive performance model for hydraulic flocculator design with polyaluminum chloride and aluminum sulfate coagulants. Karen A. Swetland, Monroe l. Weber-Shirk, and Leonard W. Lion. Journal of Environmental Engineering, submitted (2012)

## Slide 62: Floc Volcanoes
Intermittent floc volcanoes in the Floc-filter/Seds at San Nicolas
Flocs rise preferentially on one side of the sed tanks
Raw water turbidity = 4 NTU
PACl dose = 3.5 mg/L
Settled water turbidity varies between 0.5 and 4 NTU
Brainstorm! What is happening? Why does our plant do so poorly?
Notes: What do you know?
What could cause what is observed?
Which of those causes is consistent with observations?

## Slide 63: Settled Turbidity at San Nicolas
Turbidity (NTU)
Raw water
Settled water

## Slide 64: Plate Settler Problems: Temperature Gradients
Warmer water is less dense
Warm water rises
Cold water drops
Performance drops
Need a solution!
Could we further reduce residence time in sed tank so that density gradients are less significant?

## Slide 65: Design of the Inlet Diffuser
If an Floc-filter/Sed has a length of 6 m, a width of 1 m, a depth of 2 m, an upflow velocity of 1 mm/s, and a diffuser spacing () of 5 cm…
What is the port flow rate? ________________________
(50 mm)(1 m)(1 mm/s) = 50 mL/s

## Slide 66: Diffuser Slot Width
Proposed constraint is head loss in jet leaving the jet reverser (perhaps 1 cm)
Minimum width to not exceed target head loss
This head loss will improve flow distribution between diffusers
Notes: Note: No vena contracta here because the flow isn’t confined and thus there is no way for potential energy to turn into kinetic energy. Thus the jet can’t accelerate (contract) as it goes around the jet reverser.

## Slide 67: Is there a Vena Contracta?
Vena contracta is associated with a change in pressure that causes an acceleration of the fluid
The change in pressure is supported by an enclosed flow space and flow
What is the energy of the water leaving the diffuser pipe?
Prove that the flow can’t contract!
Notes: Pressure across parallel streamlines is constant. Take ascending jet at same elevation as exit from slot. Potential energy is the same. Pressure is the same. If flow accelerated it would require the pressure to drop in the jet, but the jet is always exposed to the open tank on the inner side of the jet and thus the pressure can’t be dropping along the jet.

## Slide 68: Diffuser Width
is about 380 mm/s!
Compare jet velocity with head loss through plate settlers. The momentum of this jet must be attenuated through jet expansion and floc filter.
Round up to 1/8” mold

## Slide 69: Sed Tank Inlet design Post 2021
Floc break up is likely a constraint for delivery of water to the Floc-filter/Seds.
Flow distribution and the ability to resuspend a settled floc filter are likely the most important constraints
Floc hopper needs design algorithms (highlighted by design of 1 L/s plant)

## Slide 70: Design Review
Comparing designs
  Pan-American Health Organization (CEPIS)
  Superpulsator®
  AguaClara
What is good?
What can be improved?
What could (or did) fail?

## Slide 71: Santa Rosa de Copan: CEPIS Plant Tour
Notes: https://www.youtube.com/watch?v=aLaCuq9PK7s
<iframe width="640" height="360" src="https://www.youtube.com/embed/aLaCuq9PK7s?autoplay=1&mute=1" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>

## Slide 72: CEPIS/OPS designs – Vertical Flow
Critique this design
Sludge will accumulate on the flat tank bottom
How are plate settlers suspended?
Inaccessible channels

## Slide 73: CEPIS Sed
Plate settlers and effluent launders
Launders must be perfectly level using this system
Submerged launders are easier to build with no concern if they aren’t level

## Slide 74: AguaClara Evolution
Ojojona - Vertical Flow Sedimentation (2 m)
Tamara and Marcala - sloped bottoms of the tanks (2 m)
4 Comunidades - Inlet manifold below the sloped bottoms (1.55 m) and no elevated platforms
Agalteca – Inlet manifold pipe with orifices

## Slide 75: Cuatro Comunidades

## Slide 76: Cuatro Comunidades Sludge
Notes: Mud in the bottom of the sed tank in 4 Com in May during the first cleaning. Note as Monroe inferred that there doesn’t seem to bee too much depth of accumulation in the middle of the tank; there seems to be more behind the panels that form the triangle. Note that the mud behind the panels is dark underneath (and reeks) meaning that there is some kind of biological decay occurring. That mud is very tough and doesn’t come out with just wash water, as you see in the next picture, a shovel is necessary. I think some kind of tool will always be needed to clean any plant, but the easier the mud can come out the better off for operation and water quality.

## Slide 77: Brainstorm
Why is this problem occurring?
How would you fix this problem?
What concepts might be important in obtaining a solution?
What are some of the other constraints that must be considered?

## Slide 78: Large scale circulation and poor performance is common in sedimentation tanks

## Slide 79: Floc escape at Agalteca (2009)

## Slide 80
No floc filter in this design because of flat bottom section that covers the drain

## Slide 81: Inlet Manifold Improvements at Tamara
Chart: Cumulative Percentage of the Samples

## Slide 82: Diffusers that Eliminate Circulation and Keep the Floc Filter in Suspension
Notes: This was tested at multiple plants and is much better than the manifolds that were simple pipes with a row of holes!

## Slide 83: Moroceli – Fall 2014

## Slide 86
Holes to drain beneath jet reverser were eliminated beginning in 2015.
Jet reverser
Diffusers
Inlet Manifold

## Slide 87: Steps to take an Floc-filter/Sed offline and then return it to service

## Slide 88: Block inlet water

## Slide 89: Block outlet manifold and drain tank

## Slide 90: Remove outlet Manifold

## Slide 91: Remove plate settlers

## Slide 92: Replace plate settlers

## Slide 93: Replace outlet manifold
How shall we fill this tank?

## Slide 94: Fill the tank through the outlet manifold!

## Slide 95: Remove the inlet pipe stub to return the tank to service

## Slide 96: Questions
Why do we use plate settlers?
What is the failure mechanism for plate settlers for small spacing?
Notes: 6m / 0.17m/s
4mm/s
Entrance channel design is now governed by flow distribution constraint. Don’t drop the flocs, distribute the water between sed tanks.

## Slide 97: Floc-filter/Sed Conclusions
3 processes in one tank: floc filter, sedimentation, consolidation
Eliminate the need for mechanized sludge removal by using hydraulic sludge removal
Provide the operator with options for dumping poorly flocculated or poorly clarified water

## Slide 98: Floc-filter/Sed Conclusions
Plate settlers make it possible to significantly reduce Floc-filter/Sed area
Reduced plate spacing reduces depth of Floc-filter/Sed
floc filters improve performance and provide a method to remove sludge
Flow distribution is VERY important
Hydraulic residence time of 24 minutes is sufficient for efficient clarification

## Slide 99: More sedimentation tank failure modes
Buoyant flocs
  Anaerobic sludge
  Dissolved air flotation from compressed air in the transmission line or from increased temperature
Collapsing floc filters from bad bottom geometry
Floc volcanoes from temperature increases
Curtains on windows to block sunlight
Slime from iron oxidizing bacteria