## Slide 1: Filtration Design
On removing little particles with big particles

## Slide 2: Filtration Outline
Sand Filters
  Slow sand (SSF)
  Rough Gravel (RGF)
  Dynamic Gravel (DGF)
  Rapid (RSF)
  Stacked Rapid (StaRS)
Range of applicability
Net Velocity
Hydraulics
Particle Capture theory
  Transport
  Dimensional Analysis
  Model predictions
Methods to improve performance

## Slide 3: Categorizing Filters
Surface filtration (slow sand & membrane filters)
  Particles to be removed are larger than the pore size
  Clog rapidly and large piezometric head required
  Head loss increases faster and faster as pores clog
Depth filtration (rapid sand and stacked rapid)
  Particles to be removed are much smaller than the pore size
  Require that particles collide with and attach to the media
  Can handle more solids before developing excessive head loss
  Head loss increases at a constant rate
Our focus here
Require more energy

## Slide 4: Sand Filtration Technologies
Slow (Filters→English→Slow sand→“Biosand”)
  First filters used for municipal water treatment
  Were unable to treat the turbid waters of the Ohio and Mississippi Rivers
  Can be used after rough gravel filters to extend range
Rapid (Mechanical→American→Rapid sand)
  Used in Conventional Water Treatment Facilities
  Used after flocculation and sedimentation
  High flow rates→clog 12 – 90 hr→hydraulic cleaning
Stacked Rapid Sand (StaRS)
  6 x smaller than rapid sand and self backwashing
“Biosand” is a misnomer based on a misunderstanding of SSF mechanisms. The preferred term is intermittent SSF (ISSF)
backwash
scrape
Notes: If you have water in a muddy river and you can only use 2 processes for treatment prior to chlorination, which processes would you choose?

## Slide 5: Filter range of applicability The “if it is dirty, filter it” Myth
Filter performance depends on pretreatment
1000
NTU
1
10
100
SSF
RSF+
StaRS+
With a floc blanket to extend range
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf for info on SSF and multistage

## Slide 6: Floc/Floc blanket/Plate settlers do the hard work
The amount of water wasted from each unit process is determined by the solids concentration of wasted water.
The goal is to minimize volume of wasted water: therefore maximize solids concentration of waste
Backwash water is less concentrated than floc hopper waste
  Goal is to minimize solids entering filter!
  Backwash water can be reprocessed, but that requires a pump (a good option to explore for dry season water saving)
Notes: Estimate of backwash waste from Water Quality and Treatment: A Handbook of Community Water Supplies. 5th ed. AWWA

## Slide 7: Combining Rapid Sand Filtration and pretreatment
AguaClara: Flocculation – Floc Blanket – Settle – Filter
  Able to treat very high turbidities because filter is the polishing step
  Effluent from sedimentation should be less than 2 NTU (and much lower is much better)
Conventional: Flocculate – Settle – Filter
  Same as above
Direct: add Coagulant and then Filter
  An option if raw water turbidity is always low
  less than 5 NTU

## Slide 8: Slow Sand Filtration
First filters to be used on a widespread basis
Fine sand with an effective size of 0.2 mm
Low flow rates (0.03-0.12 mm/s)
Schmutzdecke (_____ ____) forms on top of the filter (surface filtration)
  causes high head loss
  must be removed periodically
Used without coagulation/flocculation!
Turbidity should always be less than 10 NTU with a lower average to prevent rapid clogging
filter cake
Compare with sedimentation
Notes: See page 8.77 in Water Quality and Treatment: A Handbook of Community Water Supplies. Fifth edition.
This is the default technology that has been widely touted as the best option for the global south. However failures and abandonment are common.

## Slide 9
Slow Sand Filter
Notes: Part of a multiple stage filtration plant in San Pedro de Tutule, Honduras.

## Slide 10: Multistage Filtration is a land and capital intensive option
Another option for communities using surface waters
Uses no coagulants (if lucky)
Gravel roughing filters
Polished with slow sand filters
Large capital costs for construction
No coagulant costs
Labor intensive operation
Notes: http://www.atypon-link.com/TELF/doi/pdf/10.1680/wama.157.3.143.46664

## Slide 11: Multiple Stage Filtration
Dynamic
DGF
Rough
RGF
Slow
SSF
Disinfection
Clogs and shuts down plant during high turbidity event
Reduces turbidity so SSF doesn’t clog so fast

## Slide 12: Assembling Multiple Stage Filters
Notes: San Pedro de Tutle FIME plants

## Slide 13
Notes: San Pedro de Tutle FIME plants

## Slide 14
Dynamic Filter
Roughing
Slow Sand

## Slide 15: Jesus de Otoro, Honduras: Dynamic Filters

## Slide 16: Multiple Stage Filtration Options for pretreatment for SSF
Filters in series with different size media in each filter
Dynamic filter (clogs to shutdown plant)
Up flow gravel filter with multiple layers
Best option here is dynamic + Up flow with layers
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf
See section 4.3 for hint that the drainage system is the piece that requires further research. This suggests that they may still be having difficulty cleaning the sediment from these filters. Note that these filters are not easily disassembled for maintenance and thus do not meet the specifications for easy maintenance required for AguaClara plants.

## Slide 17: Up flow Roughing filter
0.08 to 0.17 mm/s
Turbidity removal is between 50% and 90%
D = 19 - 25 mm
D = 13 - 19 mm
D = 6 - 13 mm
D = 3 - 6 mm
D = 1.6 – 3 mm
overflow
From dynamic filter
Wash water
Rapid opening wash valve
Cap to prevent air entrance during washing
Exit chamber
Effluent
Manifold system
Cleaning, Impossible fittings, Maintenance, Water exit?
2 m long
5.5 mm/s during wash
50x
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf Figure 9.1

## Slide 18: First iteration of covering a roughing filter…
Covered to reduce growth of algae. What is the next logical step?
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf

## Slide 19: System Comparison: Multistage vs. AguaClara water treatment
Multistage has more expensive hardware (many large valves) and requires 10 to 20 times more land area
Multistage doesn’t use coagulants
Multistage performs poorly with turbid water
When might multistage be better than AguaClara?

## Slide 20: Net Velocity Concept for estimating plant size
Use this velocity to determine approximate total unit process area.
Similar approach for sizing any facility for comparison
Always check the velocity of unit processes to see if they are going to be cost effective
This term dominates

## Slide 21
Filter type | Velocity (mm/s) | Cleaning | Max (NTU) | pC* | Area (m2) for 1 L/s
Dynamic | 0.4 |  |  | 0 | 2.5
Roughing1 | 0.17 | 5.5 mm/s downflow |  | 0.52 | 5.9
Slow | 0.04 | Scrape surface | 10 | 0.82 | 25
Multistage | 0.033 |  | 1004 | 1.3 | 33.4
Rapid | 0.7 – 2.8 | 11 mm/s backwash | 55 | 1 | 0.55
Entrance | 8 |  |  |  | 0.125
Flocculation | 4 |  |  |  | 0.25
Sedimentation | 1 |  |  | 2.5 | 1
Floc Hopper | 5 |  |  |  | 0.2
Stacked Rapid | 1.8 x 6 | 11 mm/s backwash | 36 | 16 | 0.093
AguaClara | 0.63 |  | 10005 | 3.5 | 1.67
1 Roughing is up flow in layers
2 Based on table 5.7 https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf
3 Net velocity for scaling total plan view area of facility.
4 This assumes a target of 5 NTU in the effluent
5 Assumes a target of 0.3 NTU in the effluent (based on performance of the Atima plant)
6 Data from Tamara.
The 32 L/s plant at San Nicolas has 5.5 m2 per L/s = 0.18 mm/s (includes chemical room, bathroom, office)
Notes: Based on table 5.7 of https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf
Note that areas don’t include controls, entrance tanks, walkways, etc.
Flocculator is 2 m deep and residence time is about 500 s.
The 32 L/s plant at San Nicolas has 5.5 m^2 per L/s

## Slide 22: A factor of 20 matters!

## Slide 23: Rapid Sand Filter (Conventional US Treatment)
Sand
Gravel
Influent
Drain
Effluent
Wash water
Anthracite
Size
(mm)
0.70
0.45 - 0.55
5 - 60
Specific
Gravity
1.6
2.65
2.65
Depth
(cm)
30
45
45

## Slide 24: Rapid Sand Filter Design
Filter media
  silica sand and anthracite coal
  non-uniform media will stratify with _______ particles at the top
Filtration approach velocities
  0.7 – 2.8 mm/s
Backwash approach velocities
  set to obtain a bed porosity, f, of 0.65 to 0.70
  Fluidized bed
smaller
Similar in size to AguaClara Sed (1 mm/s)
Does water speed up or slow down when it enters the sand?

## Slide 25: Backwash (Fluidized Bed)
Sand
Gravel
Influent
Drain
Effluent
Wash water
Anthracite
Wash water is treated water!
WHY?
Only clean water should ever be on effluent side of filter!
Notes: https://www.youtube.com/watch?v=9tqk2cFDi5o#t=226

## Slide 26: Filter Hydraulics
Porosity
Sand size definitions
Clean bed head loss estimates
Backwash requirements
Low flow design challenges: the backwash dilemma

## Slide 27: Porosity
volume of voids
total volume
Example: 1 m3 of dry aquifer material weighed 1600 Kg. The aquifer material was then saturated with water and found to weigh 2000 Kg.
What is the porosity of the aquifer material?
What is the bulk density of the aquifer material?
What is the density of the aquifer material?
0.4
1600 kg/m3
2700 kg/m3

## Slide 28: Porosity
Which will have the greatest porosity?
  1 µm diameter clay
  0.2 mm diameter sand
  1 cm diameter gravel
You have been given 100 kg each of clay, sand and gravel
  What could you do to create the lowest porosity?
100 kg gravel, 100*0.4/0.6 kg sand, 100*(0.4/0.6)2 kg clay
Notes: 100 kg, 67 kg, 44 kg

## Slide 29: Expanded Bed Porosity
Pore volume + volume above bed = Expanded bed pore volume
Total expanded volume
Filter expansion ratio
Backwash porosity
Now we can relate porosity and filter expansion ratio
Notes: Sand fraction * height of sand is conserved!

## Slide 30: Sand Grading
Effective Size
  D10 - sieve size that 10% by mass of the sand passes through
  Used for filter particle removal modeling
D60 – sieve size that 60% by mass of the sand passes through
  Used for hydraulic modeling
Uniformity Coefficient = D60/D10

## Slide 31: Clean Bed Head Loss (Karmen Kozeny)
Kozeny constant
Approximately 5 for most filtration conditions
Porosity (0.4 for uniform size media)
Head loss
Flow path length (filter bed depth)
Approach velocity
Sand diameter
Kinematic viscosity
Assumes laminar flow and is valid up to Re of 6
Hagen Poiseuille
Notes: Karmen Kozeny valid up to Re of 6
Page 8.10 in Water Quality and Treatment: A Handbook of Community Water Supplies. Fifth edition.
What happens if we have an upflow RSF and we gradually increase the filtration velocity? At some point (to be determined) the pressure difference will be enough to lift the entire sand bed!

## Slide 32: Backwash Requirements – Head Loss (force balance)
For FiSand=0.4 and rSand=2650 kg/m3
=
Weight of water/Filter area
Weight of sand/Filter area
Notes: The pressure drop times the filter area is equal to the buoyant weight of the sand grains.

## Slide 33: What does this analysis miss?
Sand bed may first lift as a unit and then fall into the fluidized state
Wall shear (scale effect!!!!) and embedded pipes may prevent bed lift (or require more force than our simple force analysis suggests)
Sand will stratify if there is even a small range of sizes: Backwash velocity must be sufficient to fluidized the largest sand
Backwash initiation requires more study
Notes: Also! Dirty sand has more head loss!

## Slide 34: Backwash Requirements – Flow Rate
Kozeny
Set them equal
Backwash Head Loss (force balance)
Minimum approach velocity required to fluidize bed
Notes: Using D60 might not be conservative enough.

## Slide 35: Backwash Velocity
0.45 mm E.S. with 1.65 U.C. = D60 0.72 mm
Fluidize at 5 mm/s
30% bed expansion at 12 mm/s
PFiBw is expanded bed depth over settled bed depth
(Effective size)
Notes: This seems a bit of a stretch because we are starting with pipe flow equations. It might be better to switch to sphere sedimentation equations.
Karmen Kozeny valid up to Re of 6
Page 8.10 in Water Quality and Treatment: A Handbook of Community Water Supplies. Fifth edition.

## Slide 36: Backwash sand bed stratification
Suppose the sand stratifies in the filter bed during backwash and suppose that 10% of the bed is smaller than 0.4 mm and 10% of the sand is bigger than 0.8 mm
What is the ratio of fluidization velocity for the top of the sand bed to the fluidization velocity for the bottom of the sand bed?
Notes: Sand at top has a diameter that is ½ of the sand at the bottom. Therefore velocity to fluidize the top will be ¼ of the velocity required to fluidize the bottom. Thus seeing sand fluidize at the top of a filter bed does not guarantee that it is fluidized at the bottom.

## Slide 37: First identify a need, then invent
Slow sand – capital and labor intensive
Rapid sand – require pumps for backwash or require 6 filters working together
Neither of these are good options for small communities
Invent time!

## Slide 38: The Backwash Dilemma
Backwash velocity >> filtration velocity
Backwash water must be clean water
Backwash water sources?
  Pump it from clearwell
  Set of filters working in parallel to backwash one filter
  Filtered water stored at adequate elevation

## Slide 39: Rapid Sand Filter Set: Backwash without pumps
https://confluence.cornell.edu/display/AGUACLARA/Santa+Rosa+de+Copan
What are these two valves controlling? Reverse engineer the universe!

## Slide 40: The Low Flow Challenge: Filter Set
Assume plant flow is 6 L/s, Filtration velocity is 1.8 mm/s and backwash velocity is 9 mm/s and that a set of filters will backwash one filter
How many filters?
Total filter area?
What happens if the plant is operating at half capacity (drought conditions)?
Need filters to be smaller to be able to backwash one!

## Slide 41: Store filter water?
Try two filters and recalculate
Require a large tank and the tank must be shallow to keep filters from being really deep.
  Filters need to be able to load the tank during filtration and then take water from the tank during backwash. This is accomplished by having the filter water level VERY high during filtration and low during backwash
  Would increase AguaClara plant size by 50%! Vnet for entire plant is 0.18 mm/s
Notes: Fails the ridiculous test as named by Mickey Adelman
  Identify filtration head loss and backwash head loss

## Slide 42: The Low Flow Challenge
Requiring 6 filter boxes for a small plant is too costly and difficult to construct and maintain.
Storing filtered water requires a storage tank with a Vup less than the entire AguaClara plant!!!
If we rule out the pump option, then we have no good options…

## Slide 43: Why is this difficult?
The backwash dilemma is due to the big difference between backwash flow rates and filtration flow rates
6 filters are required if backwash velocity is 5 times the filtration velocity
If we could get those velocities to be similar or equal, then we wouldn’t need a set of 6 filters
Invention time
Notes: Brainstorm ways to get those velocities to be similar!
Decrease media density so it fluidizes at a lower velocity
Decrease media diameter so it fluidizes at a lower velocity (but that will increase head loss during filtration mode too)
Make a more compact filter. (filter in parallel, backwash in series!)

## Slide 44: Geometric Trick: Stacked Rapid Sand Filter (StaRS)
Instead of 6 filters side by side, stack them up!
Reduce backwash water volume by factor of number of layers
Notes: Optimal number of layers is a function of backwash requirements and optimal filtration velocity. We are using shallower filter beds than conventionally used and thus filter performance is expected to be poorer.

## Slide 45: Water Source for Backwash
Tradition says Filtered Water
Why not use Settled water?
Public Health trade off?
  Filter to waste after backwash is required in any case due to contamination of manifold tubing
  Use of settled water significantly simplifies the system
Same flow rate and water source during filtration and backwash!!!!
Eliminate empty clearwell failure mode

## Slide 46: StaRS Filter Fabrication
San Matías construction
Backwash operation

## Slide 47: Pipe Gallery (San Nicolas)

## Slide 48: 1999 Perspective on Conventional Treatment
For the first 75 years of this century (written in 1999), chemical clarification, granular media filtration, and chlorination were virtually the only treatment processes used in municipal water treatment. However, the past 20 years have seen a dramatic change in the water industry's approach to water treatment in which water utilities have started to seriously consider alternative treatment technologies to the traditional filtration/chlorination treatment approach. This paper identifies and discusses some of these "emerging" technologies.
CEE 4520 is about the next generation of conventional (or traditional) water treatment – the proven technologies that are used worldwide for the vast majority of municipal water treatment

## Slide 49: Eliminating 7 big valves: One valve control of a StaRS Filter
The following slides illustrate the method of using a siphon tube to initiate backwash
The filter animation only shows how the siphon will work. It doesn’t show how the inlet and outlet manifolds will be controlled
The Filter Inlet and Outlet control boxes will be designed so that water level changes* during backwash will cause all of the manifold pipes to be hydraulically separated and thus no valves will be required to turn off the inlet or outlet pipes
Notes: *This will require a slight increase in the depth of the filter to accommodate a larger change in water levels between filtration and backwash

## Slide 50: Begin Filtration

## Slide 51: Begin Backwash
Notes: Need to analyze the beginning of the siphon right after the air pressure is equalized with atmospheric pressure. It appears that we may need the height of water above the top of the siphon tube to equal the depth of submergence of the end of the siphon to initiate flow through the siphon

## Slide 52: End Backwash

## Slide 53: The big flush
Patent US2017263 - FLUSHING APPARATUS - Google Patents
Notes: Patent US2017263 - FLUSHING APPARATUS - Google Patents

## Slide 54
End Backwash cycle
What is the head loss in the sand bed between an inlet and an outlet?
What is the head loss through the sand bed + plumbing?
Constraints on depth of water in inlet box during backwash?
Notes: Backwash water level must be high enough to not pull air into the filter and low enough to not flow into the other inlets.

## Slide 55: Head loss between manifolds Assume expansion ratio of 1.3
Find depth of settled sand in 20 cm of expanded sand
Expanded depth (20 cm)
Settled depth
This is head loss per 20 cm of expanded bed!

## Slide 56
Begin Filtration cycle
Outlet box
Total filter head loss
Inlet pipe head loss

## Slide 57
End Filtration cycle
What causes water to flow through the filter bed?
____________________________
differences in piezometric head
Outlet box
Total filter head loss
Notes: Does gravity matter?
Apply the energy equation.
What must be true about the head loss for each parallel path?
What is the ratio of flows that the bottom inlet must be able to handle? If the head loss in the bottom inlet system is 10 cm during filtration, then what would it be during backwash?
What does this say about the head loss in the inlet system during filtration?
What must be true about the head loss in the pipe inlets in order to get uniform flow distribution?

## Slide 58
Backwash cycle

## Slide 61: How does water flow through StaRS Filters?
Water flows in direction of decreasing piezometric head

## Slide 62: Filter Design Constraints
Spacing between inlet pipes (or outlet pipes) must be small compared with layer depth
Filter should be able to be backwashed at the beginning of filtration cycle if needed
All inlets and outlets (except bottom inlet) must be high and dry during backwash
Kinetic energy in trunk lines and inlet/outlet pipes must be less than 10% of the clean bed head loss to achieve uniform flow distribution in sand bed*
* Edge of knowledge
Notes: See manifold notes for justification for kinetic energy guide.

## Slide 63
10 cm
Max and min filtration water levels
Inlet
Outlet
10 cm
Pipe OD
10 cm
Notes: This doesn’t have every last detail included (such as head loss over the backwash weir, but it is close.
How could you measure expansion ratio?

## Slide 64: EStaRS and OStaRS Enclosed vs. Open
Fabrication becomes difficult with filter dimensions less than 1 m x 1m
Minimum OStaRS flow rate is about 8 L/s
EStaRS doesn’t require excavation because filter is operated under vacuum for backwash

## Slide 65: StaRS Backwash Advantage
Where does the water come from that fills the filter box after the siphon is broken at the end of backwash?
Where does the water come from that slowly fills up the filter box during a filtration run?
Unlike RSF the backwash water above the StaRS bed does not pass through the sand during filtration

## Slide 66: StaRS Challenges
Inlet slotted pipes clog
  2015 replaced with
Water level changes above sand result in unnecessary water waste
Could we replace Outlet slotted pipes?

## Slide 67: StaRS Optimization
Sand Diameter – smaller diameter is more efficient at particle capture, requires a lower backwash velocity and thus a lower filtration velocity could be used
No evidence yet of breakthrough happening before max head loss. Thus shallower filters may be possible
Big goal is to eliminate slots
More research required to improve the design
Notes: Perhaps filter media size has also evolved to be large enough to cause sufficient violence during backwash to remove particles. Thus it is possible that if we try a smaller filter media size that the filter won’t clean well.

## Slide 68: Reflections
Which particles are easier to capture (big ones or small ones)? (both!!!)
Why does a rapid sand filter improve in performance in the first minutes of operation?
Why is this file called floc filtration?
Why do many water treatment facilities use dual media filtration?
Notes: Big particles are likely more easily sheared from the constriction wall.
Small particles are less likely to contact the constriction wall!
Big flocs form constrictions that then capture smaller flocs
Because it is the flocs that created constrictions that then do a better job of capturing small particles.
Dual media filters are likely used to reduce head loss or surface filtration. More research required!

## Slide 70: Conclusions…
Many different filtration technologies are available
Filters are well suited for taking clean water and making it cleaner. They are not a good choice for treating very turbid surface waters
Pretreat using flocculation/floc blanket/plate (or tube) settlers

## Slide 71: …Conclusions…
StaRS 3 main advantages over RSF
  ____________
  ______________________________________
  Single valve control
  No big valves needed!
RSF (and StaRS) require pretreatment with coagulant
Self backwashing (no pumps)
Smaller filter area required

## Slide 72: …Conclusions
RSF have pC* of 1 to 1.5 under normal conditions (max influent turbidity is about 5 NTU)
StaRS have pC* of 1 (preliminary data)
SSF have pC* of 1 to 1.5, but they perform poorly if the water contains much colloidal clay
Sand Filters CAN NOT treat high turbidity water
Notes: We need to update the StaRS pC*

## Slide 73: StaRS Design Guidelines
Settled water is divided evenly between filters that are in filtration mode
  Weir into entrance box
    need to eliminate air entrainment problem
Backwash filter gets design flow
Each filter has an overflow box
Filtered water flows over a weir into a box taking water to the distribution tank

## Slide 74: Siphon Geometry for Air trap
What must be true for the air in the siphon air trap?
  Mass of air must be conserved
    Volume of air is NOT conserved
  Pressure in the air is independent of elevation
    Depth of “submergence” (hydrostatic pressure) must be the same at both ends of the siphon!
What relationship can we use to final volume of air given initial volume of air?
  PV=nRT

## Slide 75
L10
L30
L2
H1
H2
H1
H3
H1
H2
H1
H3
Siphon Geometry
What determines how much air we trap?
What happens as head loss increases?
Success requires two things
1. Start backwash whenever desired (optional).
2. Prevent backwash from starting before reaching max head loss.
Notes: As head loss increases H1 increases. That means that some water must flow out of the end of the siphon pipe. That means that the water level in the vertical section of pipe inside the filter box must rise too! At some point we will get H1=H3 and the siphon will start flowing!

## Slide 76: Siphon Geometry for Air trap
0
1

## Slide 77: Maximum water level that can be held by siphon
Failure mode is when H1=H3 Set H1=H3, then solve for H3
This is the maximum value of H3

## Slide 79: Maximum water level that can be held by siphon
The max water level is set by the overflow weir in the inlet box
We should include a safety factor of perhaps 10 cm to ensure that the siphon doesn’t start leaking before the filter reaches max head loss
The disadvantage of a higher invert is that the water level in the filter box must be higher in order to initiate backwash.
Notes: Our previous design constraint was that the top of the U had to be below the minimum water level in the filter box so that backwash could be initiated even with a clean filter bed. We are going to eliminate that constraint and say that there is a need to backwash immediately after starting to filter that it will be necessary to block the filter outlets to raise the water level. This would be an unusual circumstance.