## Slide 1
Turbidity stops decreasing before primary filter stops growing!
Notes: How does the primary filter remove small particles?
Are plate settlers needed after a primary filter?
What determines how fast the floc/water interface rises? 100mg/L*1mm/s = 3000 mg/L * x mm/s
Why might a primary filter reduce settled water turbidity?
How is water entering the tank?
Where do the solids eventually go?
What mechanisms could result in particle aggregation in a primary filter?
It’s a filter
It’s a flocculator
Wait, filters and flocculators are really quite similar. (particles colliding and attaching)
New question: which flocs are active and which flocs are inactive in the primary filter?

## Slide 2: Primary filter observations
First order removal with respect to depth initially
Turbidity above the primary filter is similar to raw water turbidity (Dr. Casey Garland observation)
Primary particle capture may continue at primary filter depths greater than 1 m

## Slide 3: Primary filters reduce settled water turbidity
Research required to determine optimal upflow velocity
Primary filter formation requires
  All flocs be returned to the bottom of the AguaClarifier (plate settlers)
  All settled flocs must be resuspended by incoming water (jet reverser)
Primary filters need flocculators AND plate settlers!

## Slide 4: Vertical Flow Sedimentation Tanks
Have lower velocities and hence turbulence levels might be lower (plan view area is larger than width x height
Require careful attention to delivery and extraction of water
AguaClara uses channels at one end of the tanks that are connected to pipes to deliver and extract water – other geometries would be possible

## Slide 5: Stagnant Water (or Ripe for Innovation?)
State of the art in sedimentation…
  Empirical guidelines
  Little understanding of effects of temperature or of core particle properties
Last significant paper on tube settlers was published in 1978
No significant revisions to Ten State Standards section on sedimentation in the past 30 years
extra
Notes: Personal communication with Daryl Bond and Frank Kulick of Brentwood Industries
9 records in Compendex for 1884-2010 Save Search - Create Alert -
((((tube settler) WN ALL)) AND ({water treatment} WN CV))
TUBULAR SETTLERS - A TECHNICAL REVIEW. Willis, Roderick M. Source: Journal / American Water Works Association, v 70, n 6, p 331-335, Jun 1978

## Slide 6: Time to switch strategies
Shear is what we used to create collisions between particles and significantly reduce the concentration of primary particles
Shear PREVENTS particles of different sizes from colliding
We’d like to get collisions between big flocs and primary particles (We need relative motion and we can’t use shear!)
How else can we get relative motion?

## Slide 7: AguaClarifier Velocities
Notes: Give the two reasons why water accelerates when it enters the plate settlers.
It has less cross sectional area due to the space occupied by the plate settler material
It must maintained the same vertical flow velocity and it must also add a horizontal component due to the slope of the plates.

## Slide 8: Plate Settler Redesign: Ideal plate settlers
Short retention time to reduce temperature density current effect (and reduce costs)
Ideally concentrate solids to points
4 strategies to prevent floc roll up
  Upflow with large plate spacing (conventional solution)
  Upflow with W plates that concentrate solids to density currents
  Fluid flow down (particles must be sucked out- venture in inlet diffusers)
  Fluid flow sideways
Notes: Perhaps it is time to redesign plate settlers!

## Slide 9: Comparison with Q/As
a
S
L
a
Hc
H
Same answer!
As is horizontal area over which particles can settle

## Slide 10: Equation for capture velocity
Tube settler

## Slide 11: Performance ratio (conventional to plate/tube settlers)
Compare the area on which a particle can be removed
Use a single plate settler to simplify the comparison
a
S
L
Conventional capture area
Plate/tube capture area

## Slide 12: Thick Plate Settlers
a
S
L
a
hc
h
S Distance between plate settlers
B Center to center distance
T Plate settler thickness
Vertical velocity component beneath the plate settlers
Vertical velocity component between the plate settlers

## Slide 13: Thick Plate Settlers
Mass Conservation
Geometry

## Slide 14: Infinite Horizontal Plates: Boundary Conditions
negative
No slip condition
u = 0 at y = 0 and y = S
S
y
t
let
be___________
u
What can we learn about t?
x
extra

## Slide 15: Navier Stokes Flow between Plates
is average velocity between plates
We have velocity gradient as a function of average velocity
Integrate to get average velocity
extra
Notes: q is flow per unit width
u is fluid velocity as a function of location
S is spacing between the plates

## Slide 16: Laminar Flow through Circular Tubes: Equations no gravity
Max velocity when r = 0
Velocity distribution is paraboloid of revolution therefore _____________ _____________
average velocity (V) is 1/2 vmax
R is radius of the tube
extra

## Slide 17: Velocity gradient at the wall
Where dp/dx is the pressure gradient in the direction of flow NOT due to changes in elevation
Plate geometry
extra
Tube geometry
Average velocity

## Slide 18: Floc Rollup Constraint
a
Linearized (plates)
gsin(a)
g
a
Velocity at center of floc
Failure point (floc stationary)
floc diameter
Terminal velocity
extra
a
Notes: d is floc diameter
What happens when floc slides down to high shear zone?

## Slide 19: Spacing as a function of floc terminal velocity
Sedimentation velocity solved for diameter
But terminal velocity and floc diameter are related!
This is the smallest spacing that will allow a floc with a given settling velocity to remain stationary on the slope (and not be carried upward)
extra

## Slide 20: Given fractal dimension = 2

## Slide 21: Slide Capture Velocity
is the terminal sedimentation velocity (Vt) of the slowest-settling floc that can slide down an incline. Flocs with this terminal velocity (the slide velocity) will be held stationary on the incline because of a balance between gravitational forces and fluid drag. Flocs with a terminal velocity lower than will be carried out the top of the tube (i.e., “roll up”) even if they settle onto the tube wall. Thus, the slide terminal velocity represents a constraint on the ability of plate settlers to capture flocs.
What happens if the primary particles are less dense? _____
↑
extra

## Slide 22: Experimental Evidence that the Slide Capture Velocity Matters
All experiments were performed at the same settle capture velocity
Floc Roll-up and its Implications for the Spacing of Inclined Settlers Matthew W. Hurst, Michael J. Adelman, Monroe L. Weber-Shirk, Tanya S. Cabrito, Cosme Somogyi, and Leonard W. Lion. Journal of Environmental Engineering, submitted (2012)
If VSlide is bigger than VSettle, then some flocs that we expected to capture will slide out the top
extra
Notes: Floc Roll-up and its Implications for the Spacing of Inclined Settlers Matthew W. Hurst, Michael J. Adelman, Monroe L. Weber-Shirk, \\Tanya S. Cabrito, Cosme Somogyi, and Leonard W. Lion. Journal of Environmental Engineering, submitted (2012)

## Slide 23: Pressure drop (from head loss) through plate settlers
Force balance
Viscous shear
Change L to maintain capture velocity
Velocity
Shear (wall on fluid)
Notes: The shear is acting on both plates. The pressure drop is due to the shear on the plates. The areas over which the shear and pressure act are different. As the space between the plates decreases the area over which the pressure is acting decreases too. Thus the pressure increases for two reasons. Area decreases and shear increases.

## Slide 24: Plate Settler Head Loss
Head loss is tiny! We need some head loss to get reasonable flow distribution between (and within) plates. This lack of head loss may be one of the reasons for poor performance of full scale plate settlers. The velocity of any turbulent eddies or mean flow needs to be less than ______ to achieve uniform flow through plate settlers. The floc filter will end up helping us here!
4 mm/s
This represents an opportunity to improve design!
Notes: This sets the maximum velocity in the space above the plates settlers.
The lack of significant head loss through plate settlers means that any turbulence or mean velocities in the bottom of the sed tank will propagate through the plate settlers and result in non uniform distribution of flow between plates. In order to obtain reasonable uniform flow we need the velocities below the plate settlers to be close to 1 mm/s even if we use closely spaced plates. This is a daunting challenge given that the upflow velocity is 1 mm/s and given that the velocity coming from the inlet manifold ports is on the order of 100 mm/s (and thus turbulent eddies with velocities that are order 10 mm/s). The distance between the manifold ports and the bottom of the plate settlers will result in significant energy dissipation. The fact that AguaClara sed tanks are shallower than conventional design means that we need to understand and perhaps take additional steps to minimize velocities at the inlets of the plate settlers.
The AguaClara team is working to reduce velocities in the bottom of the sed tank by improving the design of the inlet manifold. The team is also evaluating the performance of small diameter tube settlers to confirm that there aren’t any other unforeseen problems caused by reducing the separation between the plate settlers.

## Slide 25: Lab scale floc filter, tube settler, floc hopper

## Slide 26
Inlet manifold/drain
Slot that runs the length of the sed tank
Sed tank cross- section showing bottom geometry
1 m
Identify the failure modes for this geometry
Notes: Flocs go down hill the whole way to the sed tank. Then they are resuspended until they land in the floc hopper and then it is down hill again to the plant drain.
There is only one place in the sed tank where flocs are resuspended.

## Slide 27: Floc Terminal Velocity does increase with diameter
How fast a particle must fall to be captured by the plate settlers
velocity here
Terminal velocity
Core particle diameter
Floc diameter
Core particle density
Water density
Water kinematic viscosity
Fractal dimension
Notes: All fractal dimensions greater than one are expected to increase the terminal velocity as the floc diameter increases.
Both floc blanket upflow velocity and plate settler capture velocity are AguaClara current design values, but are not optimized.

## Slide 28: How can you drain and then refill an AguaClarifier?
Notes: Why does the plug have a vertical tube? Serves as a handle and an air vent.

## Slide 29: Diffuser Slot Width
Proposed constraint is head loss in jet leaving the jet reverser (perhaps 1 cm)
Minimum width to not exceed target head loss
This head loss will improve flow distribution between diffusers
Notes: Note: No vena contracta here because the flow isn’t confined and thus there is no way for potential energy to turn into kinetic energy. Thus the jet can’t accelerate (contract) as it goes around the jet reverser.

## Slide 30: Diffuser Width
is about 380 mm/s!
Compare jet velocity with head loss through plate settlers. The momentum of this jet must be attenuated through jet expansion and floc filter.
Round up to 1/8” mold

## Slide 31: More sedimentation tank failure modes
Buoyant flocs
  Anaerobic sludge
  Dissolved air flotation from compressed air in the transmission line or from increased temperature
Collapsing floc filters from bad bottom geometry
Floc volcanoes from temperature increases
Curtains on windows to block sunlight
Slime from iron oxidizing bacteria