## Slide 1: Flocculator Design

## Slide 2: Overview
Mechanical Design
Analysis of hydraulic flocculators
  Vena contracta
  Head loss per bend
  Design for energy efficiency
Flocculator Design (top-down, bottom-up)
  Head loss, collision potential, residence time
  Geometry of a baffle space to obtain desired energy dissipation rate
  Flocculator Geometry
Reflections

## Slide 3: Ten State Standards
The detention time for floc formation should be at least 30 minutes with consideration to using tapered (i.e., diminishing velocity gradient) flocculation. The flow‑through velocity should be not less than 0.5 nor greater than 1.5 feet per minute.
Agitators shall be driven by variable speed drives with the peripheral speed of paddles ranging from 0.5 to 3.0 feet per second. External, non-submerged motors are preferred.
Flocculation and sedimentation basins shall be as close together as possible. The velocity of flocculated water through pipes or conduits to settling basins shall be not less than 0.5 nor greater than 1.5 feet per second. Allowances must be made to minimize turbulence at bends and changes in direction.
Baffling may be used to provide for flocculation in small plants only after consultation with the reviewing authority. The design should be such that the velocities and flows noted above will be maintained.
Hydraulic flocculators allowed only by special permission!

## Slide 4: Mechanical Flocculation
Particle collisions caused by gentle stirring
Advantage
  energy dissipation rate can be varied independent of flow rate
  simple design
Disadvantage
  potential short circuiting (some fluid moves quickly from inlet to outlet)
  moving parts in a wet environment
  Highly non-uniform energy dissipation rate

## Slide 5: Recommended G and Gq values: Turbidity or Color Removal (Mechanical flocculators)
Guidelines are given without equations
This is because we don’t yet understand the physics of flocculation
We would like to know WHY there is a difference between removing color (dissolved organics) and particles
Type | “Velocity gradient” (G) (1/s) | Gq
Low turbidity, color removal | 20-70 | 50,000-250,000
High turbidity, solids removal | 70-180 | 80,000-190,000
Sincero and Sincero, 1996 Environmental Engineering: A Design Approach
Notes: Cleasby, J. L., "Is Velocity Gradient a Valid Turbulent Flocculation Parameter?"
ASCE, Journal of Environmental Engineering, Vol. 110, No. 5, Oct.,
1984
http://dx.doi.org/10.1061/(ASCE)0733-9372(1984)110:5(875)
Why???

## Slide 6: Mechanical Design: mixing with paddles
“velocity gradient”
Drag coefficient
Projected area of paddles
Ratio of relative to absolute velocity of paddles
Reactor volume
This equation does not account for the inefficiency that is the result of the non uniform distribution of energy dissipation in mechanical flocculators

## Slide 7: Mechanical Flocculators and Energy Dissipation Rate
Model the mixing unit as a flat plate moving normal to the fluid (infinite fluid)
The maximum energy dissipation rate is given by
Closely spaced plates will have higher
V is relative velocity between fluid and plate

## Slide 8: Computational Fluid Dynamics Analysis
Flat plate normal to the flow
1 m wide
Flow was 2-D
V=1 m/s
Re = 100,000
= 0.04 W/kg
= 0.04
Energy dissipation rate
Streamlines
Notes: Ariane Walker-Horn <avw27@cornell.edu> 2015
Calculate max based on this wake equation
Calculate average based on total energy input and reactor volume.

## Slide 9: Mechanical Flocculators Summary
Waste (a small amount of) electricity
Require unnecessary mechanical components
Have a wide distribution of energy dissipation rates (highest in the wake of the paddles) that may break flocs
Have a wide distribution of particle residence times (completely mixed flow reactors)

## Slide 10: Why aren’t hydraulic flocculators used more often?
Simple construction means that there aren’t any items that private companies (venders) can sell as specialized components
Consulting firms want to be able to pass the design responsibility off to a vendor
The presumed operation flexibility of mechanical flocculators (variable speed motor driving a slow mixing unit)
Poor documentation of design approach for hydraulic flocculators (special permission required to use in the US!)
Using electricity is cool, design innovation is suspect…
Prior to AguaClara we didn’t have a design algorithm for small flocculators based on the fundamental physics

## Slide 11: AguaClara flocculator design continues to evolve rapidly
2005 - We used conventional guidelines based on velocity gradient to design the first low flow vertical flocculator
2010 - We designed using energy dissipation rate and accounted for the nonuniformity of the energy dissipation rate (q = 15 minutes)
2015 – We added obstacles to decrease the distance between expansions to make all of our flocculators have maximum collision efficiency (q = 8 minutes)
2016 – Learned that particle/floc collisions are dominated by viscous shear (not by turbulent eddies)
2019 – Learned that head loss is higher than we had predicted
202x –We increase the efficiency of removal of small particles by inventing???????

## Slide 12: AguaClara Hydraulic Flocculation Model
Probability that collision point is sticky
Diameter of primary particles
Initial distance between primary particles
Final distance between primary particles
Velocity Gradient
Flocculation time
A Hydrodynamic and surface coverage model capable of predicting settled effluent turbidity subsequent to hydraulic flocculation WH Pennock, ML Weber-Shirk, LW Lion Environmental Engineering Science 35 (12), 1273-1285 (2018)

## Slide 13: Collision Potential
The target collision potential used for the design of AguaClara plants since about 2013 has been 37,000
This equation assumes that the velocity gradient in the flocculator is uniform
Our design approach will ensure that the velocity gradient is as uniform as practically possible

## Slide 14: Flocculator Geometry
2 Channels
Upper Baffles
Port between channels
Entrance
Lower Baffles
Exit
Notes: planta de 50 Lps con 2 cámaras de sedimentación

## Slide 15: High Rate, Uniform Velocity Gradient, Plug flow, Hydraulic Flocculation
Contractions → Expansions →Turbulence → Viscous deformation of the fluid→ Collisions

## Slide 16: Fluid deformation powered by turbulent kinetic energy and damped by viscosity
Flow expansions convert potential energy into turbulent kinetic energy
Viscosity damps the eddies
Fluid deforms
Particles collide

## Slide 17: Vena Contracta around a bend?
Sluice gate (almost closed)*
  0.59
Small hole in a tank
  0.62
Exit from a pipe
  No Vena Contracta
By Lindsay Lally, Lee Hixon (Own work) [CC BY-SA 3.0 (http://creativecommons.org/licenses/by-sa/3.0) or GFDL (http://www.gnu.org/copyleft/fdl.html)], via Wikimedia Commons
* Roberson, JA; Cassidy, JJ; Chaudhry, MH. Hydraulic Engineering. John Wiley. (1995) page 217. Original reference is Henry, H.R. “Diffusion of Submerged Jets.” Discussion by M.L. Alberston, Y.B. Dai, R.A. Jensen, and Hunger Rouse, Trans. ASCE, 115, (1950)

## Slide 18: Vena Contracta (PVC ) Conclusions
Draw the most extreme streamline through the transition and determine the total change in direction
If the change in direction for most of the fluid is 90°, then the PVC is approximately 0.62
If the change in direction for most of the fluid is 180°, then the PVC is approximately 0.622=0.384
Notes: Validation Studies of Fluent Turbulence Models for Fluent Simulations of AguaClara Flocculators
AguaClara Computational Fluid Dynamics Spring 2010
Travis Stanislaus
https://confluence.cornell.edu/display/AGUACLARA/Validation+Studies+for+ANSYS+Fluent+Turbulence+Model+Simulations

## Slide 19: Head Loss coefficient for a single Baffle
the contraction coefficient for a sharp 180º bend (0.622)
Head loss in an expansion
e - expansion
Notes: Validation Studies of Fluent Turbulence Models for Fluent Simulations of AguaClara Flocculators
AguaClara Computational Fluid Dynamics Spring 2010
Travis Stanislaus
https://confluence.cornell.edu/display/AGUACLARA/Validation+Studies+for+ANSYS+Fluent+Turbulence+Model+Simulations

## Slide 20: Measurements from Hydraulic Flocculators Show Loss Coefficient > 2.6
Flow doesn’t fully expand before going around the next bend!
The velocity entering the bend is higher than we thought!
Next step is to find

## Slide 21: Plane Jets: Empirical Coefficients
Jet: , Vo
It is possible that it would be better to use this equation rather than the equation for the width to estimate the minor loss coefficient (because losses scale with velocity squared)
We began use this equation for designs in 2020
Notes: See Jets & Plumes lecture notes
https://github.com/monroews/Hydraulics/raw/master/Jets_%26_Plumes.pptx

## Slide 22: Jet Expansion Geometry for Baffles in Series
S
He
S
S
Two equations in two unknowns
Flow contraction
Flow expansion
Ljet
Must be <= S
The jet doesn’t fully expand if He/S < 5

## Slide 23: Minor loss for baffles in series*
These analytical results are a hypothesis and require confirmation either with full scale hydraulic tests or with Computational Fluid Dynamics

## Slide 24: Flocculator Efficiency
Which space between baffles is better, considering the uniformity of the energy dissipation rate?
This space with very low energy dissipation rate doesn’t contribute much

## Slide 25: L>6
Jets expand in width at the rate of approximately 1 unit in width per 10 units forward
Expansion length is 10(0.6S) = 6S
The transition to lower efficiency (less uniform velocity gradients) is related to the distance required for the jet to fully expand
Notes: Flocculators with He/S<5
We need to know what the Baffle head loss coefficient is for this case. It is possible that the head loss coefficient is larger than the 2 that we predict based on the contraction coefficient because the flow will not have fully expanded before going through the next contraction. Thus the head loss is quite possibly higher for the low H/S ratios than what we are assuming. It is important that we figure this out BEFORE we build a large flow plant with a low H/S ratio. We could either obtain a solution using CFD or by conducting laboratory experiments.
It is very likely that the flow fully expands as it goes around the 180 degree bend. Inertia will cause the higher velocity water to move toward the outside of the bend which is where the flow has separated from the baffle. Thus it is quite possible that the head loss is the same for H/S<5 as it is for H/S>5.

## Slide 26: Simplify flocculator design by designing for high efficiency
Efficiency will be a function of the variability of the energy dissipation rate
We expect a relation of the form such that efficiency is 1 when =1 and efficiency is less than 1 for higher values of
We “solve” this unknown by always designing efficient flocculators with 3<He/S<6 (or perhaps <8 assuming that efficiency doesn’t drop off rapidly)
S
S
S

## Slide 27: Obstacles and He/S vs H/S
He = H when there are no obstacles
He/S is what defines flocculator efficiency
Water
flow path
No obstacles
1 obstacle
per baffle
Obstacles
Notes: This range of H/S is necessary to ensure that there is always a solution when switching from two expansions per baffle to one expansion per baffle.

## Slide 28: Unknowns
Head loss (change in water elevation from inlet to outlet)
Residence time (t)
Baffle spacing (S)
Number of baffles (N)
Channel length (L)
Channel width (W)
Water depth (HW)
Number of channels
Number of flow expansions per baffle
Total deformation of the fluid (Gt)
Every dimension matters, but how?
Notes: We want to create a straight path to our solution.

## Slide 29: Design Considerations
The length of the flocculator channels matches the length of the sedimentation tank (thus far…)
Width of the flocculation channel?
  Minimum? ________________
  Material limitations (polycarbonate width)
  Optimize to get the desired flocculator volume given the specified length of the channels
Even or odd number of baffles depending on channel inlet and outlet conditions
Human width
Notes: planta de 50 Lps con 2 cámaras de sedimentación

## Slide 30: The Influence of GCS and GMax
The value of GCS determines the head loss through the flocculator
Maximum size of the flocs is controlled by GMax
AguaClara flocculators have a GMax that is 1.4 GCS
Casey Garland has tested GCS values as high as 550 Hz with clay-based flocs at 22°C.
  Lower G values are required at lower temperature
  Flocs with dissolved organics require lower GCS
Notes: Likely much harder to attach than to stay together once connected.
Flocs grow in low shear zones
Flocs breakup in high shear zones
Likely that initial attachment phase is more difficult than staying together once attached. Thus breakup likely doesn’t happen much in a uniform shear environment.

## Slide 31: Possible constraints
Optimize plant layout
Water level leaving flocculator must match water level entering sedimentation tank (Always)
We want an efficient flocculator (controlled by H/S ratio)
Perhaps aim for flow passages that are close to square (W=S)
Notes: Water levels must match! No pumps and no floc breakup

## Slide 32: Two design approaches
Bottom up: Start by designing one baffle space (the small details) and then work up to designing the overall size of the flocculator
  Only basis for selection of channel width would be W=S
Top down: Start by finding total volume of flocculator required and then go to the details
  Our choice

## Slide 33: Bottom up Design Approach
Assume a water depth and a channel width
Design a baffle spacing and obstacle spacing to get an efficient He/S and the target GCS
Calculate GCSq for one baffle spacing given your design
Calculate number of baffle spacings required to achieve design GCSq
Calculate length of channel required

## Slide 34: Top Down Design Approach (our choice)
Calculate the required flocculator volume
Use plant layout constraints to select an optimal channel width
Design baffles and obstacles to create the target GCS to set the baffle spacing
Fill the channels with baffles and don’t worry about a little extra space at the end of the channel that might not be used efficiently

## Slide 35: Key equations that we can use to design flocculators
Minor loss equation
Energy dissipation rate must match the rate that mechanical energy is lost*
Fluid deformation is set by the energy dissipation rate and viscosity
*On average, potential energy lost in a flow expansion is dissipated in the residence time of that flow expansion
Continuity, mass conservation

## Slide 36: Energy use (head loss) in flocculation controls velocity gradient
Some of the kinetic energy in the flow contraction…
…is dissipated through turbulence and viscosity
Given the water temperature and hence viscosity the energy dissipation produces velocity gradients
Given a total fluid deformation (GCSq), the relationship between head loss and GCS is
How can you achieve GCSq with less energy?
Notes: Reduce velocity gradient and increase residence time! Can still achieve same total fluid deformation!

## Slide 37: The design inputs for flocculation
We need collisions and thus GCSq is a logical design specification
We need to specify the maximum velocity gradient that will produce flocs large enough to be captured by the sedimentation tank (at the coldest temperature)
Higher GCS means smaller flocs and more elevation drop (head loss) through flocculator
Notes: This is in part because we don’t have a rational basis to choose the G value for flocculation. There is an economic impact of increasing head loss, so we use that constraint for now.

## Slide 38: Flocculator design begins with 3 parameters
Start with (GCS, GCSq) and coldest opearting temperature
  Calculate residence time, q
  Calculate head loss through the flocculator hFloc
GCS(and hence GCSq) increase in warmer temperatures due to decrease in viscosity
  Expansion head loss is independent of temperature
  The energy we are putting into the flocculation process is independent of temperature
  the fluid deforms less when it is cold
Sets maximum floc size possible
Sets final concentration of un-flocculated particles
Notes: We are trying to minimize cost. Setting head loss sets building height and sets flocculator volume. The best design might be minimizing the cost from those two effects.

## Slide 39: Design the reactor geometry to get the target velocity gradient
W
S
A
Kinetic energy dissipated per residence time
Continuity
is height of one expansion zone. Could be the depth of water at the end of the flocculator if the only expansion is from the 180 degree bend
This is our general equation relating velocity gradient to reactor geometry
Rectangular geometry
Notes: What are the 3 related parameters that set how much energy the flocculator uses?
Gt
Which parameter sets the spacing between baffles? (G, EDR, hl)
Which parameter sets the flocculator volume? t

## Slide 40: Solve for channel width to set constraints on viable solutions
This is the minimum channel width if we set = 3 and set the expansion height to equal water depth
As channel gets narrower the spacing between baffles gets larger.
Channels narrower than this would have barely any or negative baffle overlap!
Elevation view
Notes: What happens if I make the channel narrower and narrower? What fails?
Find the range of W
Set W
Find the range of He
Set He
Find S

## Slide 41: Meet the target He/S by decreasing the distance H between obstacles
This design was first used at the plant in San Juan Guarita in western Honduras
If it is hard, then it might not be the right solution…
We now have an alternative geometry, the Vertical-Horizontal Flocculator
Notes: We now have an alternative design

## Slide 42: Minimum number of expansions per depth of flocculator (given W)
Solve for maximum distance between expansions, , using = 6
Round up to get the minimum number of expansions per depth of the flocculator
Eliminate S
Water depth at the end of the flocculator
Distance between flow expansions

## Slide 43: Our Design Approach Given GCS and GCSq
Start big and then design the details
  Calculate volume of flocculator
  Split it into channels
  Then design baffles, and obstacles to fill the channels to get target GCS
We can use this design approach because we are assuming that we will design for high efficiency (3< <6) and thus we don’t have to add extra volume to account for inefficiencies. (Don’t forget this requirement!)

## Slide 44: Design Algorithm: Start with GCS and GCSq
Velocity gradient and flocculator volume given head loss and collision potential
Minimum channel width required to achieve >3 and required for constructability
Number of channels by taking the total width and dividing by the minimum channel width (floor)
Channel width (total width over number of channels)
Maximum distance between expansions
Minimum number of expansions per baffle space
Actual distance between expansions
Baffle spacing
Calculate the obstacle width to obtain the same jet expansion conditions as produced by the 180 degree bend
Where K is from
Notes: Can you find a place in this algorithm where we have to limit our solution to integers?

## Slide 45: Viscous Collision Potential per Flow Expansion (bottom-up perspective)
Collision potential for one flow expansion
Energy dissipation rate is energy loss per time
Collision potential is a function of velocity. This suggests that a flocculator would perform worse if the flow rate was decreased. I don’t know if anyone has ever demonstrated that!
Hydraulic residence time for one expansion zone
These are the average velocities through the expanded flow area
Height of one expansion zone (in a vertical flow flocculator)

## Slide 46: Vertical – Horizontal Flocculator for approximately 0.5 – 20 L/s
2.5 m
0.5 m
1 L/s
40 cm head loss

## Slide 47: Horizontal – Vertical Flocculator for approximately 20 – 200 L/s
7 m
2.5 m
80 L/s
1 m wide channels
40 cm head loss
Not showing pipe frames to show water path

## Slide 48: Maximum Flow for Horizontal-Vertical Flow Flocculators
Start with the equation for maximum channel width for vertical flow
Solve for Flow
This width is set by materials available to build the baffles
We can increase the maximum flow by increasing the depth of the flocculator

## Slide 49: Horizontal – Horizontal Flocculator for highest flows
10 flocculators for 20 kL/s
Channels are 4 m deep
40 cm head loss
Cynthia Chu, Dominic Grasso, Yitzy Rosenberg
49 m
64 m

## Slide 50: More details
The ports between channels should have the same cross sectional area as WS
The number of chambers (spaces between baffles) per canal (except in the last canal) is even – the number of baffles is odd
The number of chambers in the last canal is odd – the number of baffles is even
Why?

## Slide 51: What about head loss and water levels
Downstream head loss set by sed tank
Upstream depth set by head loss through the flocculator
We design based on the depth set by the sed tank (ignore the effect of head loss that increases the water depth and retention time)
We get a slightly conservative design (more collision potential than specified)

## Slide 52: Flocculator elevations (as if it were one long channel)
Water depth of sed tank inlet
Flocculator head loss
Freeboard
HFloc
0.4S
S
S
S
We ignore triangle of fluid caused by head loss when calculating residence time

## Slide 53: An interesting design No this wasn’t AguaClara…
Notes: How could you fix this?

## Slide 54: CEPIS Horizontal Flow Flocculator
Notes: Horizontal flow results in shallower flocculators for low flow rate plants. Thus vertical flocculators take up less area and thus vertical flocculators are less expensive. Also head loss has less of an impact on flow area in vertical flocculator.

## Slide 55: Reflection Questions
How does the collision potential in a flocculator change with flow rate?
  If performance deteriorates at higher flowrates, then it isn’t because of a lack of
What is the ratio of to for well designed hydraulic flocculators (extra info!)?
Why might mechanical flocculators break more flocs than hydraulic flocculators?
Notes: If we decrease flow, then Gtheta decreases!!!!
For small H/S need to take the average energy dissipation rate and multiply by 2 to get the max.
Mechanical flocculators have much higher ratio of Gmax to Gave.

## Slide 56: Reflection Questions
In baffled flocculators how many flow expansions are there IN PARALLEL?
Design thinking! Best number of parallel flow expansions might be minimum, or maximum, or some intermediate optimum
  Invent a flocculator with hundreds of parallel flow expansions
  What insight do you have about the distance between flow expansions in series (think about jet expansion!)
0.6S
0.4S
Notes: So easy! Add obstructions! Cylinders, plates, etc.

## Slide 57: Why is the AguaClara design so different from traditional designs?
Why lower GCSq?
  Uniform velocity gradient, close to plug flow, and floc blanket
Why not tapered GCS?
  Big flocs aren’t our goal and tapering is inefficient energy use
Why much higher GCS?
  We will make big flocs in the floc blanket. (need to research dissolved organics)
Why do we use GCS rather than ?
  It isn’t an average. It is an approximation.
Notes: Lower Gt because 1) more uniform
No basis for why tapered would be better. In absence of data showing improved performance when coupled with a floc blanket we simplify the design and improve energy efficiency by using constant G

## Slide 58: Conclusions
AguaClara Hydraulic flocculators have more uniform velocity gradients than mechanical flocculators
Hydraulic flocculators require a careful design to achieve the target velocity gradient
The flocculator geometry changes dramatically as the flow rate changes