## Slide 1: Clarification

## Slide 2: Topics
Introduction
Clarifier
Floc filter
Floc resuspension
Floc Hoppers
Capture velocity
Plate settlers
Floc rollup

## Slide 3: Conventional Surface Water Treatment
Screening, grit removal, flow measurement
Mechanical Rapid Mix
Mechanical Flocculation
Sedimentation
Rapid Sand Dual
Media Filtration
Disinfection
Storage
Distribution
Raw water
Coagulant
Cl2
sludge
sludge
Backwash water

## Slide 4: AguaClara Surface Water Treatment
Screening, grit removal, flow measurement
Hydraulic
Flocculation
Plate Settlers
Stacked Rapid
Sand Filtration
Storage
Distribution
Raw water
Coagulant
Cl2
sludge
sludge
Backwash water
Floc Filter
Floc Hopper
Backwash recycle proposed
Clarifier

## Slide 5: Clarifier
Dump poorly flocculated water channel
Exit Weir that controls water levels all the way upstream to the next free fall (LFOM!)
To filters
floc filter
Notes: Exercise: Tell the story of the journey of a large floc, a small floc, a rouge loner clay particle, and of a water molecule as each travels through this Clarifier.
How do plate settlers work

## Slide 6: Elements of the Clarifier
Jet reverser
Sloped surfaces so that no sludge can accumulate
Plate settlers
Effluent manifold
Influent manifold
Plate settler modules that can be removed by an operator
Diffusers that create a line jet

## Slide 7: CLarifier
How do the flocs get into the floc hopper?
What controls the water level?
How could the operator see what is in the floc hopper?
Top view of channels
End view
floc hopper
Plate settlers
floc filter

## Slide 9: We need your help to Name the Clarifier!
We’d like a name that describes what it does
Self-cleaning with floc filter and plate settlers
Much more than a sedimentation tank
I’m calling it a Clarifier in these notes temporarily

## Slide 17: Flocculation SWOT (strength, weakness opportunities, threat) for SWOT (safe water on tap)
Strength
  Rapidly reduces the primary particle concentration
  Produces flocs that can be captured by sedimentation or filtration
Weakness
  Always leaves a significant number of primary particles
  Further increases in expenditure of energy and flocculator volume don’t produce significant improvement

## Slide 18: Flocculation is unable to aggregate all primary particles
Flocs are useless in flocculators
No successful collisions between primary particles and flocs
Notes: I haven’t been able to find literature that demonstrates this effect.
Likely that the water contained within a floc simply rotates with the floc and that no new water enters the floc in a shear flow.

## Slide 19: Four sizes/types of Floc
New flocs in the floc filter
Full flocs in the floc filter
Primary particles and flocs too small to be captured by the plate settlers
Flocs that settle fast enough to be captured by the plate settlers but not fast enough to stay in the floc filter

## Slide 20: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Inlet (from flocculator)
Floc Hopper
Floc Filter
Effluent manifold
Plate Settlers
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 21: Floc Filter
Floc filter is a high concentration of a fluidized bed of flocs that in a uniform upward flow
In floc filters small particles flow through large flocs (held in place by gravity) where they can collide with small particles that are part of the floc
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Flocs are filters!
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 22: Flocs have a finite capacity to capture incoming particles
The fraction of the projected area flow that enters the floc, , is a function of the floc porosity (or fractal dimension)
No boundary layer preventing particles from entering the floc!
We are trying to figure out how to
  Preferentially waste flocs that are full
  Increase the concentration of flocs that have a low fractal dimension
I’m getting full
I’m stuffed (my fractal dimension is too big and my porosity is too small)

## Slide 23: Floc filter performance deteriorates after the floc blanket begins wasting to the floc hopper!
Too many blue flocs with filtering capacity are being wasted!
Need to invent a way to selectively waste full flocs
Floc weir begins to overflow
Notes: This is how we turn data into insights. We search for the simplest hypotheses that would be consistent with the observations.

## Slide 24: Plate Settler
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Flocs aggregate as they slide down the plate!
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 25: Flocs tumble down the plate settlers and grow larger
This creates the large flocs that can settle fast enough to stay in the floc filter from the flocs created by the flocculator
As big flocs fall from the plate settlers they break if they are bigger than the size set by the bond strength and gravity
If this aggregation weren’t happening there wouldn’t be any way for flocs to exit the plate settler!

## Slide 26: Plate Settler Feeds Floc Filter
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Flocs in free fall have a maximum size!
The maximum size of flocs in the floc filter is set by gravity
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 27: Floc maximum size based on each hemisphere trying to rotate
Each half of the floc experiences drag that tends to cause that half of the floc to rotate
Buoyancy is at 3/8 r
Drag is at greater distance from center of sphere.
Result is torque that puts lower floc bond in tension.
Buoyancy
Drag
Notes: https://en.wikipedia.org/wiki/List_of_centroids
Centroid of hemisphere is at 3/8 r

## Slide 28: Floc Filter Research

## Slide 29
Flocculator
floc filter
Tube Settlers
No sand filter….

## Slide 30
Notes: https://www.youtube.com/watch?v=pytXC-1zWhw
<iframe width="590" height="483" src="https://www.youtube.com/embed/pytXC-1zWhw" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>
<iframe width="791" height="445" src="https://www.youtube.com/embed/pytXC-1zWhw?autoplay=1&start=285&end=360" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>
How does the floc filter remove small particles?
Are plate settlers needed after a floc filter?
What determines how fast the floc/water interface rises? 100mg/L*1mm/s = 3000 mg/L * x mm/s
Why might a floc filter reduce settled water turbidity?
How is water entering the tank?
Where do the solids eventually go?
What mechanisms could result in particle aggregation in a floc filter?

## Slide 31: Floc filters are very different from flocculation
Flocculation
Shear flow
Particles can only attach to similar sized particles
Primary particle aggregation rate slows as number of concentration of primary particles decreases
Effluent contains many small flocs and a few NTU (or mg/L) of primary particles that haven’t been flocculated
Floc filter
Filtration inside flocs
Only very small particles flow into the floc filter flocs and then attach inside the floc
Full size flocculator flocs can’t attach to floc filter flocs (shear on outside of floc filter flocs is too high)
The suspension leaving the top of the floc filter contains small flocs from the flocculator as well as some primary particles

## Slide 32: Floc filter Questions
How do you design for flow rate variability?
This is complicated because the concentration of the floc filter increases as the flow rate decreases and thus the jet reverser has to work harder to maintain the suspension.
We don’t yet have equations to guide this!
Notes: What fails when the flow rate slows?

## Slide 33: Floc filter Questions
How will the operator observe the floc filter? (flashlight through the plate settlers… Can we do better?)
How could we make it work better?
  Waste only full flocs
  Add more new flocs
Notes: Perhaps split into teams here to brainstorm how to make the floc filter work better

## Slide 34: Jet Reverser
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Jet reverser is key to maintaining the floc filter in suspension
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 35: Clarifier Bottom Geometry determines if floc filter builds
Flat bottom
Jet Reverser
Floc Hopper
Upflow velocity is 1 mm/s

## Slide 36: floc filter Resuspender
Flat bottom
Centered jet
Offset jet

## Slide 37: floc filter Resuspender
Inlet diffuser
How does this animation violate the laws of physics?
Can a settled floc filter be resuspended? (yes, at least sometimes)
Floc pickup location
Jet reverser
Diffuser tubes flattened to achieve a continuous jet of water the entire length of the Clarifier

## Slide 38: The jet reverser creates a vertical jet that resuspends settled flocs
All surfaces must transport particles to a resuspension zone
Sludge produces gas that suspends particles
Clarifiers should have zero sludge
Notes: May have application in other fluidized bed reactors too! No patents – you can use this new technology
<iframe width="640" height="360" src="https://www.youtube.com/embed/oHcKJD_OdfI?autoplay=1&mute=1&start=388&end=398&showinfo=0&rel=0" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>

## Slide 39: The jet deflects more when it has less momentum
Failure occurs below jet velocity of 75 mm/s
8.9 mm Jet Diameter
3.9 mm Jet Diameter
Jet
Jet
Current of settled flocs
Current of settled flocs
<

## Slide 40: Design of the Inlet Diffuser
If a Clarifier has a length of 6 m, a width of 1 m, a depth of 2 m, an upflow velocity of 1 mm/s, and a diffuser center to center spacing () of 5 cm…
What is the flow rate from one diffuser? ________________________
Notes: (50 mm)(1 m)(1 mm/s) = 50 mL/s

## Slide 41: Is there a Vena Contracta?
In a vena contracta, the fluid is forced to accelerate because there is a sudden change of direction that forces the water into a smaller flow space
Here there is a gradual change in direction and the water is not being forced into a smaller space
Apply Bernoulli! Pressure is the same! Elevation is the same! Therefore velocity must be the same!
No vena contracta here
Notes: Pressure across parallel streamlines is constant. Take ascending jet at same elevation as exit from slot. Potential energy is the same. Pressure is the same. If flow accelerated it would require the pressure to drop in the jet, but the jet is always exposed to the open tank on the inner side of the jet and thus the pressure can’t be dropping along the jet.

## Slide 42: Jet velocity constraints: a min and a max
Based on shear in the jet exiting the diffusers
Very limited data showing floc blanket collapse for at low jet velocities

## Slide 43: Diffuser Dimensions
View from the bottom

## Slide 44: Floc Hopper
Floc hopper is where excess particles accumulate and then are wasted at a high concentration
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 45: Self-cleaning, sludge-free Clarifier (without using electricity)
Notes: Note that red dye can be removed by Polyaluminum chloride!

## Slide 46: Floc Hopper Requirements
Weir controls the depth of the floc filter
Floc filter flow rate into the floc hopper is a function of the mass flux of particles into the sed tank
Flocs in the floc filter settle at a rate equal to the upflow velocity (1 mm/s)
The area required for consolidation could be based on max raw water turbidity and the corresponding floc filter concentration
  More work needed for a model for the floc filter concentration
*ff = floc filter
Notes: If influent concentration is 20 mg/L, and floc filter is 2000 mg/L, then what is the flow rate into the floc hopper

## Slide 47: Previous state-of-the-art… SUPERPULSATOR® Clarifier
Notes: https://www.youtube.com/watch?v=UNhygQov69Q
Why is pulsator needed?
Which end of the sed tank will have flocs rising rapidly? (two reasons)
<iframe width="640" height="360" src="https://www.youtube.com/embed/UNhygQov69Q?autoplay=1&mute=1&start=68&stop=214" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>

## Slide 48: Why is there pulsing flow in a SuperPulsator?
What failed when they didn’t pulse?
What problem were they trying to solve?
Can we solve that problem a better way?
Will sludge accumulate and go anaerobic?
Notes: Sludge slowly buries more and more of the inlet manifold system.

## Slide 49: Clarification!
How do we design a tank so that particles are separated from the water?
We will begin by looking at how simple sedimentation tanks (big rectangular or cylindrical open tanks) are supposed to work
Then we will explore plate settlers

## Slide 50: Horizontal Flow Clarifier
How much time is required for water to pass through the tank? _____
How far must a particle fall to reach the bottom of the tank (worst case)? _____
How fast must the particle fall?
H
W
L
entrance
exit
q
H
Settle Capture velocity: Property of the sedimentation tank. The slowest settling particle that the sedimentation tank captures reliably.
Will it remove any smaller particles? ___
Yes
Notes: How do I design a sed tank to capture 40 um flocs?

## Slide 51: Vertical Flow Clarifier
How much time is required for water to pass through the tank? _____
How far must a particle fall relative to the fluid to not be carried out the exit? _____
How fast must the particle fall (relative to the fluid)?
H
W
L
entrance
exit
q
H
Will any smaller particles be captured? ______________________________ ______________________________
Only if they collide and grow so they have a terminal velocity > vc

## Slide 52: Settle Capture Velocity Guidelines
Based on tube settlers
  0.12 – 0.36 mm/s
Based on Horizontal flow tanks
  0.24 to 0.72 mm/s
AguaClara adopted 0.12 mm/s in an effort to reduce effluent turbidity as much as possible because AguaClara wasn’t using filters
Now we have the connection between temperature, velocity gradient in the flocculator and jet reverser, and the plate settler capture velocity
Surface Water Treatment for Communities in Developing Countries. Christopher R. Schulz,Daniel A. Okun
https://www.brentwoodindustries.com/water-wastewater-products/tube-settlers/

## Slide 53: Plate Settler
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Plate settlers capture flocs that settle faster than a velocity that we will calculate next!
Plate settlers flocculate flocs and return them to the floc filter!
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 54: Plate Settlers Capture Particles that settle faster than the plate settler capture velocity
Notes: How do we know charge neutralization doesn’t explain flocculation
Floc aggregation begins even with very small dosages of coagulant long before the surface charge is neutralized
No transition in flocculation performance as the coagulant dose is gradually varied over a very wide range
No evidence of charge reversal causing deterioration in performance
A single physics-based model describes the full range of flocculation from low to high coagulant dosages
Coagulant nanoparticles are so large that they easily extend through the double layer and hence can directly bridge between two negatively charged particles
No one has been able to develop equations describing the role of charge neutralization
Confusion in the literature about whether WTPs use charge neutralization or sweep floc. No quantification of how you would know which hypothesized mechanism is operative

## Slide 55: 3 Requirements for Plate Settler Success
The floc must be able to settle to the surface of a plate or tube settler
  Settle capture velocity
It must NOT slide or roll up the incline
  Slide capture velocity
It must roll down the plate and combine with other flocs to increase its terminal velocity so it can fall back into the floc filter (and become a contributing member of the floc filter)

## Slide 56: Critical path for capture
S
L
H
Critical path for capture
a
a

## Slide 57: Settle Capture Velocity for Plate (and Tube) Settlers
S
L
How far must particle settle to reach lower plate?
Path for critical particle?
Hc
What is total vertical distance that particle will travel?
H
What is net vertical velocity?
Particle velocity
a
a

## Slide 58: Equate times to obtain the capture velocity
Time to travel distance Hc
Time to travel distance H
=
This ratio represents the plan view area reduction factor!
Notes: The ratio of the upflow velocity to the capture velocity is really a measure of the reduction in tank area that is possible from using plate settlers. It is easy to get a factor of 10 reduction.

## Slide 59: Clarifier vertical velocity components
Plate Settlers
Floc filter
Floc hopper
Inlet manifold
Outlet manifold
Notes: This was tested at multiple plants and is much better than the manifolds that were simple pipes with a row of holes!

## Slide 60: Plate Settler Design (AguaClara approach)
Upflow velocity (determines size of tanks) (1 mm/s)
  If floc filter is a goal then needs to be approximately 1 mm/s
Capture velocity (0.12 mm/s)
  Must capture the large flocs produced by the flocculator (and jet reverser)
Plate angle (60 deg)
  self cleaning (60 deg works well)
Spacing (2.5 cm)
  Clogging (not a problem at 2.5 cm)
  floc roll up: Will the floc slide down? (next topic in the notes!)
Length of the plate settlers
  will be the parameter that we calculate

## Slide 61: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Inlet (from flocculator)
Floc Hopper
Floc Filter
Effluent manifold
Plate Settlers
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 62: Reflections on learning
How do you remember what happens in lecture?
What do you do to be actively engaged?

## Slide 63: Plate Settler Spacing Constraints: Floc Rollup
Why do we care? – What is the connection to sustainability?
Why not use the standard design?

## Slide 64: Floc Roll Up Solution Scheme: Another failure mode
Find the velocity gradient next to the plate
Find the fluid velocity at the center of the floc
Find the terminal velocity of the floc down the plate (for the case of zero velocity fluid)
Set those two velocities equal for the critical case of no movement
a
gsin(a)
g
a
a

## Slide 65: Minimum Plate Settler Spacing
Assume fractal dimension of 2
Given that AguaClara uses a lower upflow velocity, , than many plate settler designs it is okay to use more closely spaced plates, S.
This failure mode will show up only with very low density core particles and cold water
Notes: plateAN = 60 * u.deg
vz = 1.2 * u.mm/u.s

## Slide 66: Plate Settler Spacing effects
Plate settler spacing has a strong influence on sedimentation tank depth
Diminishing effect for small S
Maintaining spacing becomes more challenging for small S because the plates are quite flexible
Too small an S will fail!
5 cm
2.5 cm
1 cm

## Slide 67: Plate Settler Conclusions…
Designed to capture flocs with sedimentation velocities greater than the settle capture velocity
Spacing determines the ability of the flocs to roll down the incline

## Slide 68: Plate Settler Confusions…
We need a basis for choosing a settle capture velocity based on overall plant performance*
Smaller spacings have diminishing returns in terms of sedimentation tank depth. So for now we are using 2.5 cm.
Flocs made from natural organic matter may be less dense, more prone to floc rollup, and require larger spacing between plate settlers
* Predictive performance model for hydraulic flocculator design with polyaluminum chloride and aluminum sulfate coagulants. Karen A. Swetland, Monroe l. Weber-Shirk, and Leonard W. Lion. Journal of Environmental Engineering, submitted (2012)

## Slide 69: Floc Volcanoes: An example of a failure mode in sedimentation tanks
Intermittent floc volcanoes in the Clarifiers at San Nicolas
Flocs rise preferentially on one side of the sed tanks
Raw water turbidity = 4 NTU
PACl dose = 3.5 mg/L
Settled water turbidity varies between 0.5 and 4 NTU
Brainstorm! What is happening? Why does our plant do so poorly?
Notes: What do you know?
What could cause what is observed?
Which of those causes is consistent with observations?

## Slide 70: Settled Turbidity at San Nicolas
Turbidity (NTU)
Raw water
Settled water

## Slide 71: Plate Settler Problems: Temperature Gradients
Warmer water is less dense
Warm water rises
Cold water drops
Performance drops
Need a solution!
Not sure WHY
Could we further reduce residence time in floc filter and plate settlers so that density gradients are less significant?

## Slide 72: Sed Tank Inlet design Opportunities as of 2022
Floc break up is likely a constraint for delivery of water to the Floc-filter/plate settlers.
Flow distribution and the ability to resuspend a settled floc filter are likely the most important constraints
For reasonable flow distribution, the inlet manifold has to be larger in diameter if we reduce the jet velocity to avoid breaking up flocs. We need an invention that will enable us to use smaller diameter inlet manifolds to keep costs down!

## Slide 73: Design Review
Comparing designs
  Pan-American Health Organization (CEPIS)
  Superpulsator® (we already looked at this one)
  AguaClara
What is good?
What can be improved?
What could (or did) fail?

## Slide 74: Santa Rosa de Copan: CEPIS Plant Tour
Notes: https://www.youtube.com/watch?v=aLaCuq9PK7s
<iframe width="640" height="360" src="https://www.youtube.com/embed/aLaCuq9PK7s?autoplay=1&mute=1" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture" allowfullscreen></iframe>

## Slide 75: CEPIS/OPS designs – Vertical Flow
Critique this design
Sludge will accumulate on the flat tank bottom
How are plate settlers suspended?
Inaccessible channels
Access to bottom of tank?
Notes: CAPÍTULO 4
DECANTADORES LAMINARES

## Slide 76: CEPIS Sed
Plate settlers and outlet manifolds
Outlet Manifolds must be perfectly level using this system (orifice elevation sets water elevation!)
Submerged launders are easier to build with no concern if they aren’t level
Channels for inlet and outlet

## Slide 77: AguaClara Evolution
Ojojona - Vertical Flow Sedimentation (2 m)
Tamara and Marcala - sloped bottoms of the tanks (2 m)
4 Comunidades - Inlet manifold below the sloped bottoms (1.55 m) and no elevated platforms
Agalteca – Inlet manifold pipe with orifices

## Slide 78: Cuatro Comunidades
Inlet channel
Vertical chimney

## Slide 79: Cuatro Comunidades Sludge
Notes: Mud in the bottom of the sed tank in 4 Com in May during the first cleaning. Note as Monroe inferred that there doesn’t seem to be too much depth of accumulation in the middle of the tank; there seems to be more behind the panels that form the triangle. Note that the mud behind the panels is dark underneath (and reeks) meaning that there is some kind of biological decay occurring. That mud is very tough and doesn’t come out with just wash water, as you see in the next picture, a shovel is necessary. I think some kind of tool will always be needed to clean any plant, but the easier the mud can come out the better off for operation and water quality.

## Slide 80: Brainstorm
Why is this problem occurring?
How would you fix this problem?
What concepts might be important in obtaining a solution?
What are some of the other constraints that must be considered?

## Slide 81: Floc escape at Agalteca (2009)
See page 185 of Integrated Design and Operation of Water Treatment Facilities by Kawamura
“For many plants it is common for the water in the middle of the tank to be clear, yet have a lot of floc rise at the end of the tank.”
“indicates density flow”
“Block off the last 10 to 20 ft…”

## Slide 82: Large scale circulation and poor performance is common in sedimentation tanks
This is an inertia problem, not a density problem!

## Slide 83
No floc filter in this design because of flat bottom section that covers the drain

## Slide 84: Inlet Manifold Improvements at Tamara
Chart: Cumulative Percentage of the Samples

## Slide 85: Diffusers that Eliminate Circulation and Keep the Floc Filter in Suspension
Plate Settlers
Floc filter
Floc hopper
Inlet manifold
Outlet manifold
Notes: This was tested at multiple plants and is much better than the manifolds that were simple pipes with a row of holes!

## Slide 86: Floc hopper
Floc hopper
Floc weir
Sludge drain

## Slide 87: Moroceli – Fall 2014
Floc hopper
Port for outlet manifold
Port for inlet manifold
Floc weir

## Slide 88
Mold to reduce the pipe diameter
Holes drilled to ID of mold

## Slide 89
Pipe with reduced diameter end

## Slide 90
Holes to drain beneath jet reverser were eliminated beginning in 2015.
Jet reverser
Diffusers
Inlet Manifold

## Slide 91: Diffusers direct a jet of water into the jet reverser
Floc pickup location
Diffusers
Inlet Manifold
Jet reverser
Plate settlers

## Slide 93: Clarifier inlet and outlet
Inlet manifold
Outlet manifold
Floc filter top surface
Water surface
diffusers
Jet reverser
Inlet channel
Outlet channel
Collector channel
Outlet weir
Flocculated water dump channel
Clarifier bay drain

## Slide 94
Floc Hopper
Plate settlers
Floc filter
Inlet channel
Outlet channel

## Slide 95: Steps to take an Clarifier offline and then return it to service

## Slide 96: Block inlet water

## Slide 97: Block outlet manifold and drain tank

## Slide 98: Remove outlet Manifold

## Slide 99: Remove plate settlers

## Slide 100: Replace plate settlers

## Slide 101: Replace outlet manifold
How shall we fill this tank?

## Slide 102: Fill the tank through the outlet manifold!

## Slide 103: Remove the inlet pipe stub to return the tank to service

## Slide 104: Questions
Why do we use plate settlers?
What is the failure mechanism for plate settlers for small spacing?
How do flocs end up in the floc filter?
How fast does the floc filter settle into a pile of sludge when the flow is stopped?
Notes: 6m / 0.17m/s
4mm/s
Entrance channel design is now governed by flow distribution constraint. Don’t drop the flocs, distribute the water between sed tanks.

## Slide 105: Clarifier Conclusions
3 processes in one tank: floc filter, sedimentation, consolidation
Eliminate the need for mechanized sludge removal by using hydraulic sludge removal
Provide the operator with options for dumping poorly flocculated or poorly clarified water

## Slide 106: Clarifier Conclusions
Plate settlers make it possible to significantly reduce Clarifier area
Reduced plate spacing reduces depth of Clarifier
Floc filters improve performance and provide a method to remove sludge
Flow distribution is VERY important
Hydraulic residence time of 24 minutes is sufficient for efficient clarification

## Slide 107: Invention Opportunities
Increase the concentration of flocs that can act as filters in the floc filter
  Floc recycle
  Selective wasting of full flocs
Decrease the required diameter of the inlet manifold

## Slide 108: Coagulant dose setting based on rapid settling of flocculated water
Plant operators will set a target particle count
If particle count is too high the coagulant dose will be increased
Goal: obtain a faster indication of whether the coagulant dose is correct and use the AguaClara flocculation model to propose a change in the dose
Submerged tube settler that will remove flocs
Flocculator
Particle counter

## Slide 109
Inlet manifold
Diffuser
Jet reverser
Plate settlers
Outlet manifold
Floc hopper
Floc filter
Floc weir
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs