## Slide 1: Flow Control and Measurement
Creativity without a trip
Variations on a drip
Giving head loss the slip
Chemical doses that don’t dip
Here’s a tip!
We can use smart fluids to eliminate software, computers, and electronics!

## Slide 2: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 3: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 4: Applications of Constant Flow
POU treatment devices (Point of Use)
  clay pot filters
  SSF (slow sand filters)
  Arsenic and fluoride removal devices
Reagent addition for community treatment processes
  Alum or Poly Aluminum Chloride (PACl) ____________
  Calcium or sodium hypochlorite for ____________
  Sodium carbonate for _____________
  Hydrochloric acid to prevent ______________________________
A flow control device that maintains a constant dose as the main flow varies (and automatically shuts off when the main flow stops)
coagulation
disinfection
pH control
calcium carbonate precipitation

## Slide 5: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 6: If you had electricity…
Metering pumps (positive displacement)
  Pistons
  Gears
  Peristaltic
  Diaphragm
Valves with feedback from flow sensors
So an alternative would be to raise the per capita income and provide RELIABLE electrical service to everyone…
But a simpler solution with fewer moving parts would be better!

## Slide 7: A couple of observations…
Municipal water treatment often fails due to unreliable chemical dosing of chlorine and coagulants
Failure modes include
  Inability to easily set the target dose
  Lack of easy method for operators to monitor flow
  Poor designs that don’t maintain a constant dose

## Slide 8: What caused this innovation?
Conscientious operators
Resourceful technicians

## Slide 9: Dosing at a large city Water Treatment Plant in Asia
One 25 kg block of alum at a time
Placed in the channel carrying raw water into the plant

## Slide 10: Salt water electrolytic chorine generators

## Slide 11: Chlorine tablet chlorinators
Notes: We notice that water treatment plants are failing because of poor control of chemical feeds.
We could conclude that the solution is to provide a better supply chain for fixing pumps.
AguaClara is taking a different route.
Let’s invent technologies that are more robust and that can be more easily maintained.

## Slide 12: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 14: The Challenge of Chemical Metering (Hypochlorinator)
What is the simplest representation that captures the fluid mechanics of this system?
Raw water entering distribution tank
Overflow tube
PVC valve
PVC pipe
Access door to distribution tank
Chlorine drip
Chlorine solution
Access door to hypochlorinator tank

## Slide 15: Hole in a bucket doesn’t give a constant flow rate
Vena contracta
Orifice
This is NOT a minor loss coefficient
It is the ratio of the vena contracta area to the orifice area
Q is flow rate [volume/time]

## Slide 16: Finding Q(t) for a tank-valve hypochlorinator [Two unknowns (Q, h)]
Our goal:
To determine the height (h) of chlorine in the tank and its flow rate out of the tank (Q) as a function of time (t)
Water source pipe
Valve
Tank
Q
h

## Slide 17: Derived equation for Q(t) through a hypochlorinator

## Slide 18: Reflections
Let the discharge to atmosphere be located at the elevation of the bottom of the tank…
When does the flow rate go to zero?
What is the average flow rate during this process if the tank is drained completely?
How could you modify the design to keep Q more constant?

## Slide 19: Effect of tank height above valve
Case 1:
h0=50 m
hTank = 1 m tDesign=4 days
Case 2:
h0=1 m
hTank = 1 m tDesign=4 days

## Slide 20: Brainstorm: Constant Flow
Why did the previous systems not provide constant flow of chlorine?
Why is this hard?
What are the desired properties of the device that meters chemicals into a water treatment plant?
Notes: The varying head from the stock tank is a big problem.
We need a constant head AND the ability for the operator to vary the flow
Elegant simplicity
Few moving parts
Easy for the operator to set the chemical dose (rather than flow)

## Slide 21: A related tangent… Design a drain system for a flocculator
*Flocculator highly, highly simplified to show drain
ΣKe is the sum of all minor loss coefficients for the drain system, including entrance and exit losses and the flow expansion caused by the elbow

## Slide 22: A related tangent… Design a drain system for a sed tank
Sedimentation tank drain also adds another minor loss for an open valve

## Slide 23: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 24: Constant Head: Floats
orifice
VERY Flexible hose
Head can be varied by changing buoyancy of float
Supercritical open channel flow!
Unaffected by downstream conditions!

## Slide 25: Hypochlorinator with float design
Raw water entering distribution tank
Overflow tube
Valve
Chlorine drip
Float
Transparent flexible tube
Orifice

## Slide 26: Floating Bowl
Adjust the flow by changing the rocks
Need to make adjustments INSIDE the checmical tank
Rocks are submerged in the chemical
Safety issues
Creative, but not ideal

## Slide 27: Constant Head: Overflow Tanks
Surface tension effects here
What controls the flow?

## Slide 28: Constant Head: Marriot bottle
A simple constant head device
Why is pressure at the top of the filter independent of water level in the Marriot bottle?
What is the head loss for this filter?
Disadvantage? ___________
batch system

## Slide 29: Constant Head: Float Valve
Float adjusts opening to maintain relatively constant water level in lower tank (independent of upper tank level)
NOT Flow Control!
?
Force balance on float valve?

## Slide 30: Our goal is to adjust the flowrate and then maintain constant flow
Head (or available energy to push fluid through the flow resistance) (voltage drop)
Flow resistance (resistor)
  ____________________________________
  ____________________________________
  ____________________________________
Vary either the head or the flow resistance to vary the flow rate (current)
  Vary head by adjusting the constant head tank elevation or the outlet elevation of a flexible tube
  Vary orifice size (flow resistance) by adjusting a valve
Orifice i.e. small hole or restriction
Long straight small diameter tube
Porous media

## Slide 31: Float valve and small tube variable head
Flow control device
Small diameter tubing
hL
chemical stock tank
straight
^
If laminar flow Hagen – Poiseuille applies. If we also
neglect minor losses,
Notes: Peter von Bucher
Presidential Prez: Alana Jonat
Executive Mastermind: Roslyn Odum

## Slide 32: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 33: Hypochorinator Fix
http://web.mit.edu/d-lab/honduras.htm
What is good?
How could you
improve this system?
What might fail?
Safety hazards?
Notes: http://web.mit.edu/d-lab/honduras.htm

## Slide 34: AguaClara Technologies
“Almost linear” Flow Controller
Linear Flow Orifice Meter
Linear Chemical Dose Controller

## Slide 35: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 36: AguaClara approach to flow control
Controlled variable head
  Float valve creates constant elevation of fluid at inlet to flow control system
  Vary head loss by varying elevation of the end of a flexible tube
Head loss element
  Long straight small diameter tube
  We didn’t realize the necessity of keeping the tube straight until 2012 and thus our early flow controllers had curved dosing tubes

## Slide 37
Holes to choose the dose
Rapid Mix
Tube from the stock tank
Air vent
Raw water
Float valve
Long, “straight,” flexible tube
0 point is at water level

## Slide 38
Raw water
In our first flow controllers we didn’t realize how important it was that the flow resistance tube be straight! We ignored minor losses and minor losses weren’t minor!
Hagen–Poiseuille:
Is only true if, in the “straight” flexible tube,
There is laminar flow
Minor losses can be neglected

## Slide 39: Early Flow Controllers
Nonlinear relationship between flow and height of end of tube because of curved tubing!

## Slide 40: Dose Controller: The QC Control Problem
How could we design a device that would maintain the chemical dose (C) as the flow (Q) through the plant varies?
Somehow connect a flow measurement device to a flow controller (lever!)
Flow controller has a (mostly) linear response
Need height in entrance tank to vary linearly with the plant flow rate – solution is The Linear Flow Orifice Meter (LFOM)
Dose is the chemical concentration in the water

## Slide 41: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 42: Linear Flow Orifice Meter
Sutro Weir is difficult to machine
Mimic the Sutro weir using a pattern of holes that are easily machined
Install on a section of PVC pipe in the entrance tank
Used at all AguaClara Plants except the first plant (Ojojona)
Invented by AguaClara team member David Railsback, 2007
See extra 3

## Slide 43: Weir flow-head Proportionality
V-notch
Rectangular
Sutro
Exponent of h is 1, linear!

## Slide 44: Linear Orifice Meter
Photo by Lindsay France

## Slide 45: Overview
Fluids Review
Applications of flow control
If you had electricity
Hole in a bucket
Constant head devices
  Floating bowl
  Overflow tanks
  Marriot bottle
  Float valve
Hypochlorinators in Honduras
AguaClara “Almost Linear” Flow Controller
AguaClara Linear Flow Orifice Meter
AguaClara Linear Chemical Dose Controller
Ctrl + click the pictures to go to each section!

## Slide 46: Linear Chemical Dose Controller (CDC)
Combine the linear flow controller and the linear flow orifice meter to create a Linear Dose Controller
Flow of chemical proportional to flow of plant (chemical turns off when plant turns off)
Directly adjustable chemical dose
Can be applied to all chemical feeds (coagulant and chlorine)
Note: This is NOT an automated dose device because the operator still has to set the dose
See extra 4

## Slide 47
Dosing tubes
Stock Tank of coagulant
Lever
LFOM
Float
Constant head tank
Float valve
Dose slider
Purge valves
Open channel supercritical flow
Drop tube
Lever
counterweight
Notes: This is a basic schematic of what research and design teams have come up with after many years of work. The stock tank holds a stock chemical solution which is connected to a constant head tank. The constant head tank is regulated by a float valve which keeps the chemical depth constant. A large diameter tube leads from the stock tank to one or more small diameter long straight dosing tubes. A large diameter flexible leads to a drop tube with “open channel super critical flow”, where the chemical flows to be added to the plant’s influent water. The drop tube is connected to a lever via a slider. The plant operator sets the slider at the desired coagulant dose based upon characteristics of the influent water. The float attached to the lever changes position as flow rate into the plant changes, thus changing the elevation of the large diameter tube’s outlet, and maintaining a constant chemical dose.

## Slide 48
Decrease dose

## Slide 49
Increase dose

## Slide 50
Notes: This is a basic schematic of what research and design teams have come up with after many years of work. The stock tank holds a stock chemical solution which is connected to a constant head tank. The constant head tank is regulated by a float valve which keeps the chemical depth constant. A large diameter tube leads from the stock tank to one or more small diameter long straight dosing tubes. A large diameter flexible leads to a drop tube with “open channel super critical flow”, where the chemical flows to be added to the plant’s influent water. The drop tube is connected to a lever via a slider. The plant operator sets the slider at the desired coagulant dose based upon characteristics of the influent water. The float attached to the lever changes position as flow rate into the plant changes, thus changing the elevation of the large diameter tube’s outlet, and maintaining a constant chemical dose.

## Slide 51
Half flow

## Slide 52
Plant off

## Slide 53
Constant Level Tanks
1 for chlorine
1 for coagulant
Spare Constant Head Tanks when maintenance needs to be done on the originals

## Slide 54
1 slider for chlorine
1 slider for coagulant

## Slide 56
Lever
Constant Level Tanks
Linear Flow Orifice Meter
Coagulant Dosing Tubes
Chlorine Dosing Tubes

## Slide 58
Atima doser: Three 1/8” diameter tubes, 1.93 m long, 187.5 g/L stock solution of PACl, 5 to 48 mg/L dose range.
Lever
Constant Level Tank
Coagulant Stock Tank
Linear Flow Orifice Meter
Dosing Tubes
Flow calibration column
Notes: Dosificador: 3 mangueras de 1/8" diámetro interno, 1.93m longitud, concentración madre de 187.5 g/L de PAC, dosis máxima 48 mg/L, dosis mínima 5 mg/L.

## Slide 59: Linear Chemical Dose Controller (CDC): A key technology for high performing plants
The operator sets the dose directly
No need for calculations
Visual confirmation
More improvements are possible!
  Make it modular
  Prevent air bubbles from blocking flow
  Make it easier to remove calcium carbonate scale

## Slide 60: Modular: Constant Level Tanks
coagulant tanks
chlorine tanks

## Slide 61: Design specifications for the float valve
The float valve has an orifice that restricts the flow of the chemical and that dominates the head loss between stock tank and constant head tank. Different float valves have different sizes of orifices.
Chemical Feed Tank
Why are we concerned with the orifice head loss?
Where else is there head loss?
Is this a minimum or a maximum orifice diameter?
Why not increase Dh?
Notes: We must also design the tubing diameter that delivers the chemical to the constant head tank
If the orifice head loss is too large the float valve will end up controlling the flow rate when the stock tank begins to empty.
This is the minimum orifice diameter. Larger would be okay.
We could increase deltah, but that raises the stock tank and the plant operator has to fill this stock tank and climb stairs to get to it.

## Slide 62: Constraints on flow controller Dosing tube design
Flow must be laminar (Re<2100)
Minor losses must be small (small V!)
  It took us a while to discover how critical this constraint is!
  Use oversized barbed fittings!
Dosing tube must “be reasonable” length which might mean shorter than an available wall in the plant.
Designing dose controllers over a wide range of chemical flow rates requires good engineering (we are still working on this!)
How can I get a shorter tube?
Notes: Get a shorter tube by using a smaller diameter tube. May need to use multiple smaller diameter tubes.

## Slide 63: Making the CDC linear: minimizing minor losses
Calibrate at max flow
Neglecting minor losses
Simple linear model
Reality

## Slide 64: CDC dosing tubes: diameter constraints

## Slide 65: CDC dosing tubes: length constraints
Notes: If the tube isn’t operating at the maximum flow possible for that tube, then it needs to be made even longer to generate the target head loss.

## Slide 66: CDC Design Algorithm
Calculate the maximum flow rate through each available dosing tube diameter that keeps error due to minor losses below 10%.
Calculate the total chemical flow rate that would be required by the treatment system for the maximum chemical dose and the maximum allowable stock concentration.
Calculate the number of dosing tubes required if the tubes flow at maximum capacity (round up)
Calculate the length of dosing tube(s) that correspond to each available tube diameter.
Select the longest dosing tube that is shorter than the maximum tube length allowable based on geometric constraints.
Select the dosing tube diameter and flow rate corresponding to the selected tube length.
Click here to get the full design and derivation
Notes: https://confluence.cornell.edu/download/attachments/77267239/LCDC_ASCE.pdf?version=1&modificationDate=1345649734000

## Slide 67: Dose Controller Accuracy
Float valves only reduce the magnitude of the fluctuations in level (constant level tanks aren’t truly constant level!)
Surface tension effects at the location where the fluid switches from closed conduit to open channel flow (the end of the dosing tube) could cause errors of a few millimeters
The weight of the tubing and slide supported by the lever will apply different amounts of torque to the lever depending on the dose chosen. This determines the required diameter of the float

## Slide 68: Maximum Plant Flow Rate Using Linear Flow Controller
Assume the PACl concentration is 160 g/L, the maximum PACl dose is 30 mg/L, and the maximum flow in a 5 mm diameter dosing tube is about 8.7 mL/s.
Mass conservation
P = Plant
C = Chemical Feed
What is the solution for larger plants? ___________
Multiple tubes
Notes: We could use a single PVC pipe that is then filled with 5 mm diameter tubes so that there is only one plumbing connection.

## Slide 69: Dose Control Summary
Laminar tube flow and linear flow orifice meters
  Coagulant dosing for plants with flow rates less than about 200 L/s
  Chlorine dose controllers even for larger plants
These devices are robust AND a good design requires excellent attention to details
  No small parts to lose
  No leaks
  Compatible with chlorine (watch out for the O-rings in PVC valves)
  Locally sourced materials if possible
  Dosing tubes must be straight
  Must account for viscosity of the chemical
  Minor losses must be minor!
  Removing calcium carbonate scale must be easy
  Must have redundancy for ease of maintenance