## Slide 1: Flocculator Design

## Slide 2: Overview
Flocculation definition and regulation
Mechanical Design
Hydraulic conventional design
Fractals
Collisions
  Predictive model
Conclusions
Surface coverage

## Slide 3: Ten State Standards
The detention time for floc formation should be at least 30 minutes with consideration to using tapered (i.e., diminishing velocity gradient) flocculation. The flow‑through velocity should be not less than 0.5 nor greater than 1.5 feet per minute.
Agitators shall be driven by variable speed drives with the peripheral speed of paddles ranging from 0.5 to 3.0 feet per second. External, non-submerged motors are preferred.
Flocculation and sedimentation basins shall be as close together as possible. The velocity of flocculated water through pipes or conduits to settling basins shall be not less than 0.5 nor greater than 1.5 feet per second. Allowances must be made to minimize turbulence at bends and changes in direction.
Baffling may be used to provide for flocculation in small plants only after consultation with the reviewing authority. The design should be such that the velocities and flows noted above will be maintained.
http://10statesstandards.com/waterrev2012.pdf
Hydraulic flocculators allowed only by special permission!

## Slide 4: Mechanical Flocculation
Particle collisions caused by gentle stirring
Advantage
  energy dissipation rate can be varied independent of flow rate
Disadvantage
  potential short circuiting (some fluid moves quickly from inlet to outlet)
  moving parts in a wet environment
  Highly nonuniform energy dissipation rate

## Slide 5: Recommended G and Gq values: Turbidity or Color Removal (Mechanical flocculators)
Type | “Velocity gradient” (G) (1/s) | Energy Dissipation Rate ()+ | Gq | q* (minute)
Low turbidity, color removal | 20-70 | 0.4 – 4.9 | 50,000-250,000 | 11 - 210
High turbidity, solids removal | 70-180 | 4.9 - 32 | 80,000-190,000 | 7 - 45
Type | “Velocity gradient” (G) (1/s) |  | Gq | q* (minute)
Low turbidity, color removal | 20-70 | 0.4 – 4.9 | 50,000-250,000 | 11 - 210
High turbidity, solids removal | 70-180 | 4.9 - 32 | 80,000-190,000 | 7 - 45
Sincero and Sincero, 1996 Environmental Engineering: A Design Approach
* Calculated based on G and Gq guidelines
+ average value assuming viscosity is 1 mm2/s
Notes: Cleasby, J. L., "Is Velocity Gradient a Valid Turbulent Flocculation Parameter?"
ASCE, Journal of Environmental Engineering, Vol. 110, No. 5, Oct.,
1984
http://dx.doi.org/10.1061/(ASCE)0733-9372(1984)110:5(875)
Why???

## Slide 6: Mechanical Design: mixing with paddles
“velocity gradient”
Drag coefficient
Projected area of paddles
Ratio of relative to absolute velocity of paddles
Reactor volume
extra

## Slide 7: Mechanical Flocculators and Energy Dissipation Rate
Model the mixing unit as a flat plate moving normal to the fluid (infinite fluid)
The maximum energy dissipation rate is given by
Closely spaced plates will have higher
V is relative velocity between fluid and plate

## Slide 8: Computational Fluid Dynamics Analysis
Flat plate normal to the flow
1 m wide
Flow was 2-D
V=1 m/s
Re = 100,000
= 0.04 W/kg
= 0.04
Energy dissipation rate
Streamlines
Notes: Ariane Walker-Horn <avw27@cornell.edu> 2015
Calculate max based on this wake equation
Calculate average based on total energy input and reactor volume.

## Slide 9: What is for mechanical flocculators?
The maximum velocity for mixing units given by 10 State Standards is 3 ft/s
No minimum plate width is specified
For narrow plates is comparable to rapid mix!
Mechanical flocculators may be breaking flocs in the wake of the mixer
Nonuniformity of the energy dissipation rate is an inefficient use of energy
http://10statesstandards.com/waterrev2012.pdf

## Slide 10: Uniformity of mixing requires
“Flocculation reactors should be designed to have relatively uniform mixing intensities throughout the reactor.”
“If the mixing intensity varies considerably across the reactor, substantial breakup will occur in the portions of the reactor with the highest intensities, thereby acting against the flocculation desired.”
Benjamin and Lawler. Water Quality Engineering: Physical/Chemical Treatment Processes (page 833)

## Slide 11: Mechanical Flocculators Summary
Waste (a small amount of) electricity
Require unnecessary mechanical components
Have a wide distribution of energy dissipation rates (highest in the wake of the paddles) that may break flocs
Have a wide distribution of particle residence times (completely mixed flow reactors)
extra

## Slide 12: Why aren’t hydraulic flocculators used more often?
Simple construction means that there aren’t any items that private companies (venders) can sell as specialized components
Consulting firms want to be able to pass the design responsibility off to a vendor
The presumed operation flexibility of mechanical flocculators (variable speed motor driving a slow mixing unit)
Poor documentation of design approach for hydraulic flocculators (special permission required to use in the US!)
Using electricity is cool, design innovation is suspect…
Prior to AguaClara we didn’t have a design algorithm for small flocculators based on the fundamental physics

## Slide 13: AguaClara flocculator design continues to evolve rapidly
2005 - We used conventional guidelines based on velocity gradient to design the first low flow vertical flocculator
2010 - We designed using energy dissipation rate and accounted for the nonuniformity of the energy dissipation rate (q = 15 minutes)
2015 – We added obstacles to decrease the distance between expansions to make all of our flocculators have maximum collision efficiency (q = 8 minutes)
2016 – Learned that particle/floc collisions are dominated by viscous shear (not by turbulent eddies)
202x –We increase the efficiency of removal of small particles (q = 1 minute) ???????

## Slide 14: Flocculator Geometry
2 Channels
Upper Baffles
Port between channels
Entrance
Lower Baffles
Exit
extra
Notes: planta de 50 Lps con 2 cámaras de sedimentación

## Slide 16: AguaClara Hydraulic Flocculation Model
Probability that collision point is sticky
Diameter of primary particles
Initial distance between primary particles
Final distance between primary particles
Velocity Gradient
Flocculation time
A Hydrodynamic and surface coverage model capable of predicting settled effluent turbidity subsequent to hydraulic flocculation WH Pennock, ML Weber-Shirk, LW Lion Environmental Engineering Science 35 (12), 1273-1285 (2018)

## Slide 17: Floc model for viscous dominated collisions
Velocity gradient
Initial particle spacing
Flocculation time
Rate constant (model fitting parameter)
A function of fractional surface coverage of particle by coagulant
Particle diameter
Notes: What does the operator control?
What changes in a rain event?
What does the design engineer control?

## Slide 18: Overview
Analysis of hydraulic flocculators
  Vena contracta
  Head loss per bend
  Design for energy efficiency
Flocculator Design (top-down, bottom-up)
  Head loss, collision potential, residence time
  Geometry of a baffle space to obtain desired energy dissipation rate
Reflections

## Slide 19: 10 flocculators for 20 kL/s (465 MGD)
Yesterday’s student design!
Channels are 4 m deep
40 cm head loss
Cynthia Chu, Dominic Grasso, Yitzy Rosenberg
49 m
64 m

## Slide 20: High Rate, Uniform Velocity Gradient, Plug flow, Hydraulic Flocculation
Contractions → Expansions →Turbulence → Viscous deformation of the fluid→ Collisions
Additional flow contractions to achieve more uniform velocity gradients (for flows below 44 L/s – 1 MGD)

## Slide 23: Fluid deformation powered by turbulent kinetic energy and damped by viscosity

## Slide 24: Vena Contracta around a bend?
Sluice gate (almost closed)*
  0.59
Small hole in a tank
  0.62
Exit from a pipe
  No Vena Contracta
By Lindsay Lally, Lee Hixon (Own work) [CC BY-SA 3.0 (http://creativecommons.org/licenses/by-sa/3.0) or GFDL (http://www.gnu.org/copyleft/fdl.html)], via Wikimedia Commons
* Roberson, JA; Cassidy, JJ; Chaudhry, MH. Hydraulic Engineering. John Wiley. (1995) page 217. Original reference is Henry, H.R. “Diffusion of Submerged Jets.” Discussion by M.L. Alberston, Y.B. Dai, R.A. Jensen, and Hunger Rouse, Trans. ASCE, 115, (1950)

## Slide 25: Vena Contracta (PVC ) Conclusions
Draw the most extreme streamline through the transition and determine the total change in direction
If the change in direction for most of the fluid is 90°, then the PVC is approximately 0.62
If the change in direction for most of the fluid is 180°, then the PVC is approximately 0.622=0.384
Notes: Validation Studies of Fluent Turbulence Models for Fluent Simulations of AguaClara Flocculators
AguaClara Computational Fluid Dynamics Spring 2010
Travis Stanislaus
https://confluence.cornell.edu/display/AGUACLARA/Validation+Studies+for+ANSYS+Fluent+Turbulence+Model+Simulations

## Slide 26: Head Loss coefficient for a Baffle
the contraction coefficient for a sharp 180º bend (0.622)
Head loss in an expansion
We need to measure this in one of the new AguaClara plants!
e - expansion
Notes: Validation Studies of Fluent Turbulence Models for Fluent Simulations of AguaClara Flocculators
AguaClara Computational Fluid Dynamics Spring 2010
Travis Stanislaus
https://confluence.cornell.edu/display/AGUACLARA/Validation+Studies+for+ANSYS+Fluent+Turbulence+Model+Simulations

## Slide 27: Flocculator Efficiency
Which space between baffles is better, considering the uniformity of the energy dissipation rate?
This space with very low energy dissipation rate doesn’t contribute much

## Slide 28: L>5
Jets expand in width at the rate of approximately 1 unit in width per 10 units forward
Expansion length is 10(0.6S) = 6S
The transition to lower efficiency (less uniform velocity gradients) is related to the distance required for the jet to fully expand
Notes: Flocculators with He/S<5
We need to know what the Baffle head loss coefficient is for this case. It is possible that the head loss coefficient is larger than the 2 that we predict based on the contraction coefficient because the flow will not have fully expanded before going through the next contraction. Thus the head loss is quite possibly higher for the low H/S ratios than what we are assuming. It is important that we figure this out BEFORE we build a large flow plant with a low H/S ratio. We could either obtain a solution using CFD or by conducting laboratory experiments.
It is very likely that the flow fully expands as it goes around the 180 degree bend. Inertia will cause the higher velocity water to move toward the outside of the bend which is where the flow has separated from the baffle. Thus it is quite possible that the head loss is the same for H/S<5 as it is for H/S>5.

## Slide 29: Simplify flocculator design by designing for high efficiency
Efficiency will be a function of the variability of the energy dissipation rate
We expect a relation of the form such that efficiency is 1 when =1 and efficiency is less than 1 for higher values of
We “solve” this unknown by always designing efficient flocculators with 3<He/S<6
S
S
S

## Slide 30: Obstacles and He/S vs H/S
He = H when there are no obstacles
He/S is what defines flocculator efficiency
Water
flow path
No obstacles
1 obstacle
per baffle
Obstacles
Notes: This range of H/S is necessary to ensure that there is always a solution when switching from two expansions per baffle to one expansion per baffle.

## Slide 31: Our Approach: Always efficient
Add obstacles to have a maximum ratio of between 3 and 6.
Our flocculator energy efficiency is ≈ 100%
6 = 2*3! Guarantees a solution as we switch from 2 expansions to 1 expansion per baffle
30 L/s
10 L/s
Notes: This range of H/S is necessary to ensure that there is always a solution when switching from two expansions per baffle to one expansion per baffle.

## Slide 32: Viscous collisions or inertial collisions
Prior to 2016 I had assumed that the appropriate length scale comparison was particle separation distance and Kolmogorov length scale – thus concluded inertia was important
Particle separation distances are smaller than inner viscous length scale
Collisions in turbulent flocculators are dominated by viscosity (fluid shear, not turbulent eddies)*
2016
* Edge of knowledge

## Slide 33: Collision Potential
The target collision potential used for the design of AguaClara plants since about 2013 has been 37,000
The PF300 has a GCSq of about 20,000

## Slide 34: Unknowns
Head loss
Residence time
Baffle spacing
Number of baffles
Channel length
Channel width
Water depth
Number of channels
Number of flow expansions per baffle
Total deformation of the fluid
Every dimension matters, but how?
Notes: We want to create a straight path to our solution.

## Slide 35: Design Considerations
The length of the flocculator channels matches the length of the sedimentation tank (thus far…)
Width of the flocculation channel?
  Minimum? ________________
  Material limitations (polycarbonate or concrete)
  Vary to optimize flocculation efficiency (function of geometry)
Human width
Notes: planta de 50 Lps con 2 cámaras de sedimentación

## Slide 36: More Design Considerations
Even number of channels for AguaClara design (to keep chemical dose controller near stock tanks), but this may change if flocculators get smaller
Even or odd number of baffles depending on channel inlet and outlet conditions

## Slide 37: The Influence of GCS and GMax
The value of GCS determines the head loss through the flocculator
Maximum size of the flocs is controlled by GMax
AguaClara flocculators have a GMax that is 1.4 GCS
Summer 2015 new designs have head loss of approximately 40 cm and thus increased GCS
  Expect smaller flocs (but still captured by plate settlers)
  Less sedimentation of flocs in flocculator
  Smaller flocculator
Casey Garland has tested GCS values as high as 340 Hz
Notes: Likely much harder to attach than to stay together once connected.
Flocs grow in low shear zones
Flocs breakup in high shear zones
Likely that initial attachment phase is more difficult than staying together once attached. Thus breakup likely doesn’t happen much in a uniform shear environment.

## Slide 38: Possible constraints
Optimize plant layout
Water level leaving flocculator must match water level entering sedimentation tank
We want an efficient flocculator (H/S ratio)
Minimize plant cost with tradeoff between head loss (function of GCS) and volume (function of q)
Notes: Water levels must match! No pumps and no floc breakup

## Slide 39: Two design approaches
Bottom up: Start by designing one baffle space (the small details) and then work up to designing the overall size of the flocculator
  No basis for selection of channel width
Top down: Start by finding total volume of flocculator required and then go to the details
  Our choice

## Slide 40: Bottom up Design Approach
Assume a water depth and a channel width
Design a baffle spacing and obstacle spacing to get an efficient He/S and the target GCS
Calculate GCSq for one baffle spacing given your design
Calculate number of baffle spacings required to achieve design GCSq
Calculate length of channel required

## Slide 41: Top Down Design Approach (our choice)
Calculate the required flocculator volume
Use plant layout constraints to select an optimal channel width
Design baffles and obstacles to create the target GCS to set the baffle spacing
Fill the channels with baffles and don’t worry about a little extra space at the end of the channel that might not be used efficiently

## Slide 42: Key equations that we can use to design flocculators
Minor loss equation
Energy dissipation rate must match the rate that mechanical energy is lost*
Fluid deformation is set by the energy dissipation rate and viscosity
*On average, potential energy lost in a flow expansion is dissipated in the residence time of that flow expansion
Continuity, mass conservation

## Slide 43: Energy use (head loss) in flocculation controls velocity gradient
Some of the kinetic energy in the flow contraction…
…is dissipated through turbulence and viscosity
Given the water temperature and hence viscosity the energy dissipation produces velocity gradients
Given a total fluid deformation (GCSq), the relationship between head loss and GCS is
How can you achieve GCSq with less energy?
Notes: Reduce velocity gradient and increase residence time! Can still achieve same total fluid deformation!

## Slide 44: The design inputs for flocculation
We need collisions and thus GCSq is a logical design specification
We need to specify energy use
  Velocity gradient - GCS
  Energy dissipation rate -
  Total head loss -
Or specify q
More time helps diffusion of coagulant nanoparticles to clay surfaces
Higher GCS means smaller flocs and more elevation drop (head loss) through flocculator
Current approach
Notes: This is in part because we don’t have a rational basis to choose the G value for flocculation. There is an economic impact of increasing head loss, so we use that constraint for now.

## Slide 45: Our current choice of parameter that sets energy input is head loss
Head loss is independent of temperature
Velocity gradient is f(temperature)
Start with (GCS, GCSq) and cold temperature
  Calculate q
  Calculate hFloc
Start with (hFloc, GCSq) and cold temperature
  Calculate GCS
  Calculate q
GCS(and hence GCSq) will increase when the flocculator is operated at warmer temperatures due to decrease in viscosity
Current approach
Option 2
Option 1
Notes: We are trying to minimize cost. Setting head loss sets building height and sets flocculator volume. The best design might be minimizing the cost from those two effects.

## Slide 46: Design the reactor geometry to get the target velocity gradient
W
S
A
Kinetic energy dissipated per residence time
Continuity
is height of one expansion zone. Could be the depth of water at the end of the flocculator if the only expansion is from the 180 degree bend
This is our general equation relating velocity gradient to reactor geometry
Rectangular geometry
Notes: What are the 3 related parameters that set how much energy the flocculator uses?
Gt
Which parameter sets the spacing between baffles? (G, EDR, hl)
Which parameter sets the flocculator volume? t

## Slide 47: Solve for channel width to set constraints on viable solutions
This is the minimum channel width if we set = 3 and set the expansion height to equal water depth
As channel gets narrower the spacing between baffles gets larger.
Channels narrower than this would have barely any or negative baffle overlap!
Elevation view
Notes: What happens if I make the channel narrower and narrower? What fails?
Find the range of W
Set W
Find the range of He
Set He
Find S

## Slide 48: Meet the target He/S by decreasing the distance H between obstacles
This design was first used at the plant in San Juan Guarita in western Honduras
Notes: [PLACEHOLDER TEXT]

## Slide 49: Minimum number of expansions per depth of flocculator (given W)
Solve for maximum distance between expansions, , using = 6
Round up to get the minimum number of expansions per depth of the flocculator
Eliminate S
Water depth at the end of the flocculator
Distance between flow expansions

## Slide 50: Our Design Approach Given energy ( or GCS) and GCSq
Start big and then design the details
  Calculate volume of flocculator
  Split it into channels
  Then design baffles, and obstacles to fill the channels to get target GCS
We can use this design approach because we are assuming that we will design for high efficiency (3< <6) and thus we don’t have to add extra volume to account for inefficiencies. (Don’t forget this requirement!)
(AguaClara approach as of summer 2015)

## Slide 51: Design Algorithm (as of 2016) Start with and GCSq
Velocity gradient and flocculator volume given head loss and collision potential
Minimum channel width required to achieve >3 and required for constructability
Number of channels by taking the total width and dividing by the minimum channel width (floor)
Channel width (total width over number of channels)
Maximum distance between expansions
Minimum number of expansions per baffle space
Actual distance between expansions
Baffle spacing
Calculate the obstacle width to obtain the same jet expansion conditions as produced by the 180 degree bend

## Slide 52: Viscous Collision Potential per Flow Expansion (bottom-up perspective)
Collision potential for one flow expansion
Energy dissipation rate is energy loss per time
Collision potential is a function of velocity. This suggests that a flocculator would perform poorly if the flow rate was decreased. I don’t know if anyone has ever demonstrated that!
Hydraulic residence time for one expansion zone
These are the average velocities through the expanded flow area
Height of one expansion zone (in a vertical flow flocculator)

## Slide 53: Maximum Flow for Vertical Flow Flocculators
Start with the equation for maximum channel width for vertical flow
Solve for Flow

## Slide 54: Almost Real Designs (Flocculator exit depth of 2 m)
What sets maximum channel width?
What sets minimum channel width?
Why this cycle of channel widths?
Human hip
Sheet width
Number of channels
1
2
3
4
5
Here we allowed odd number of channels
Notes: Max is sheet width
Min is half sheet (hip width) or the width required to not get an H/S less than 3.
Cycle is due to increasing number of channels (integers)

## Slide 55: Design Scaling (Design Engine version 7099)
50 L/s
0.56 m wide channels
6.68 m long
10 L/s
0.53 m wide channels
4.33 m long
70 L/s
0.72 m wide channels
7.27 m long
20 L/s
0.55 m wide channels
5.90 m long
Notes: Extra obstacles for 10 and 20 L/s.
Channels get wider

## Slide 56: More details
The ports between channels should have the same cross sectional area as WS
The number of chambers per canal (except in the last canal) is even – the number of baffles is odd
The number of chambers in the last canal is odd – the number of baffles is even
Why?

## Slide 57: What about head loss and water levels
Downstream head loss set by sed tank
Upstream depth set by head loss through the flocculator
We design based on the depth set by the sed tank (ignore the effect of head loss that increases the water depth and retention time)
We get a slightly conservative design (more collision potential than specified)

## Slide 58: Flocculator elevations (as if it were one long channel)
Water depth of sed tank inlet
Flocculator head loss
Freeboard
HFloc
0.4S
S
S
S
We ignore triangle of fluid caused by head loss when calculating residence time

## Slide 59: An interesting design No this wasn’t AguaClara…
Notes: How could you fix this?

## Slide 60: CEPIS Horizontal Flow Flocculator
Notes: Horizontal flow results in shallower flocculators for low flow rate plants. Thus vertical flocculators take up less area and thus vertical flocculators are less expensive. Also head loss has less of an impact on flow area in vertical flocculator.

## Slide 61: Reflection Questions
How does the collision potential in a flocculator change with flow rate?
What is the ratio of to for well designed hydraulic flocculators (extra info!)?
Why might mechanical flocculators break more flocs than hydraulic flocculators?
Notes: If we decrease flow, then Gtheta decreases!!!!
For small H/S need to take the average energy dissipation rate and multiply by 2 to get the max.

## Slide 62: Reflection Questions
What are some alternate geometries?
How else could you generate head loss to create collisions?
0.6S
0.4S
Notes: So easy! Add obstructions! Cylinders, plates, etc.

## Slide 63: Reflection Questions
What is the relationship between potential energy loss and the average velocity gradient in a flocculator?
How did AguaClara get around the 45 cm limitation?
How does the non uniformity of e (or G) influence efficiency of energy use?

## Slide 64: Why is the AguaClara design so different from traditional designs?
Why lower GCSq?
  Uniform velocity gradient
  Close to plug flow (no short circuiting)
Why not tapered GCS?
  Big flocs aren’t our goal! No reason for tapering!
Why much higher GCS?
  We will make big flocs in the floc blanket
Why do we use GCS rather than ?
  It isn’t an average. It is an approximation.
Notes: Lower Gt because 1) more uniform
No basis for why tapered would be better. In absence of data showing improved performance when coupled with a floc blanket we simplify the design and improve energy efficiency by using constant G

## Slide 65: Conclusions
Energy dissipation rate determines the spacing of the baffles.
Energy is used most efficiently to create collisions when the energy dissipation rate is uniform. Therefore H/S between 3 and 6 is best.
Collision potential is a function of geometry and a function of flow rate

## Slide 66: The Energy Dissipation Rate isn’t uniform
Ideally (for optimal efficiency) the flocculator would have a completely uniform energy dissipation rate
We can evaluate the energy dissipation rate uniformity of various designs as a function of H/S
extra

## Slide 67: Estimating the ratio
Definition of
True for large where the jet fully expands before the next turn
Energy lost
time
Control volume analysis
extra
Notes: THE INFLUENCE OF VISCOSITY ON MIXING IN JET REACTORS
Jo BALDYGA, J. R. BOURNE* and R. V. GHOLAP
Chemical Engineering Science, Vol. 50, No. 12, pp. 1877-1880, 1995
It is expected that P.Jet is a function of the jet geometry.

## Slide 68: Estimating
The transition value for /S is at 5 (from CFD analysis) (this is our weakest assumption)
has a value of 2 for <5 (CFD analysis and Haarhoff, 2001)
has a value of for > 5
Solve for when = 5
extra
Notes: “Overlap ratios of less than 5 result in normalized G-values of less than 1.5.” Towards optimal design parameters for around-the-end hydraulic flocculators, Johannes Haarhoff and Jeremia J. van der Walt.
Journal of Water Supply: Research and Technology—AQUA | 50.3 | 2001
We can move from a G ratio to a EDR ratio by squaring the G ratio.

## Slide 69: Results of the CFD analysis and our model equations
e is more uniform when H/S is between 3 and 6.
For <5
Prior to 2015 all AguaClara designs had an H/S > 5.
Future designs will have 3 < < 6
extra
Notes: These results require a Pi.PlaneJet value of 0.0124

## Slide 70: Use a Pipe with orifices to make a flocculator for small flows (S=D)
Continuity
Here we use Ke from typical baffled flocculators and H/S of 6 to minimize number of chips required. Round up to nearest inner pipe diameter? Or round down to get higher velocities to prevent sedimentation?
DPipe
hL
DOrifice
Here we assume that S is like D
extra

## Slide 71: Estimate the orifice diameter
The head loss for these orifices spaced so closely may be less than what we calculate
  Vena contracta may not be as severe for orifices that are close to the inner diameter of the pipe
  Insufficient length for full expansion before next orifice
We need to estimate Ke!
extra

## Slide 72: Estimate the orifice diameter using the required value of Ke given the actual pipe ID
Need to find actual Ke given actual pipe diameter to develop target G. The actual Ke will increase to get the same head loss given the slower velocity in the larger diameter pipe.
Replace residence time with volume/Q
extra
https://neutrium.net/fluid_flow/pressure-loss-from-fittings-expansion-and-reduction-in-pipe-size/

## Slide 73: Use a Pipe with orifices to make a flocculator for small flows (H = D)
Continuity
Round to nearest inner pipe diameter? Or round down to get higher velocities to prevent sedimentation?
DPipe
hL
DOrifice
Here we assume that H is like D
extra