## Slide 1: Flocculation Introduction

## Slide 2: Overview
Options for separating contaminants from water
Sedimentation doesn’t remove pathogens fast enough!
Ganging up on gravity (flocculation)
Sticky nanoparticles

## Slide 3: Exploit differences between water and the contaminant to separate them
Difference | Floc Blanket | Sedimentation | Filtration
Size | ✓ | ✓ | ✓
Density | ✓ | ✓ | 
Molecular Polarity |  |  | 
Magnetism |  |  | 
Electrical charge |  |  | 
Optical properties |  |  | 
Size and Density both influence terminal velocity

## Slide 4: Sedimentation: Particle Terminal Fall Velocity
projected
Identify forces

## Slide 5: Drag Coefficient on a Sphere
laminar
turbulent
turbulent boundary
Stokes Law

## Slide 6: Sedimentation is too slow for pathogens and clay
10-12
10
10-6
10-3

## Slide 7: Gravity separation is awesome, but we need help
How could we increase the sedimentation rate of small particles?
Increase d (stick particles together)
Increase g (centrifuge)
Decrease viscosity (increase temperature)
Increase density difference
(dissolved air flotation)
Notes: Deriving the equations that show what matters is a useful skill in design. I’m currently working on designing our stacked rapid sand filters and I went through a long derivation to determine the size of the pipes needed for the filter. And then I looked at the equation and realized that I could get better results if I changed my assumptions about how the filter would be built! If I had done an iterative or numerical analysis I would have missed that insight!

## Slide 8: Flocculation
A process where we create the conditions so that particles can attach to each other
Requires two things
  Transport
  Attachment
    The point of contact must be sticky
The goal of flocculation is to have all particles attach to each other and form flocs that settle faster
Notes: A process that transforms a turbid suspension of tiny particles into a turbid suspension of big particles!
Requires
  Sticky particles (splattered with adhesive nanoparticles)
  Successful collisions between particles
Flocs are fractals (“the same from near as from far”)
The goal of flocculation is to reduce the number of small particles (that haven’t been flocculated)
One goal is to understand why some particles are always left behind (turbidity after sedimentation)
Another goal is to learn how to design a flocculator

## Slide 9: Transport processes to create collisions between particles (clay and pathogens)
Transport mechanism | Does it help flocculation?
Differential sedimentation (larger particles settle faster) | No! Not significant because particles of different sizes can’t get close enough to each other to attach because of the boundary layer thickness on the larger particle
Turbulent mixing | No! The smallest turbulent eddies are so large that both particles are in the same eddy
Viscous shear (fluid deformation) | YES!!!!!
Molecular diffusion | No! Too slow for particles that are smaller than about 1 mm (very important for transporting coagulant nanoparticles and dissolved organic molecules)
Molecular forces (Van der Waals force etc.) | No! Only act over lengths of a few nm and thus are not significant

## Slide 10: Fluids deform continuously (velocity gradient - G) given a stress (t)
Velocity gradient
Dynamic viscosity
Kinematic viscosity

## Slide 11: Definitions
Coagulation: The process of adding a sticky solid phase material (adhesive nanoparticles) that attaches to the particles so they can attach to each other (the topic of these notes)
Flocculation: The process of producing collisions between particles to create flocs (aggregates) (next set of notes)

## Slide 12: Aluminum Sulfate Chemistry Alum [Al2(SO4)3*14.3H2O]
A widely used coagulant
Typically 10 mg/L to 100 mg/L alum is used (0.9 to 9 mg/L as Al)
High concentrations (stock solutions) don’t precipitate because the pH is low
The alum precipitates when it blends with the water in the water treatment plant
The primary reaction produces Al(OH)3
Al2(SO4)3 + 6H2O2Al(OH)3 + 6H+ + 3SO4-2
pH = -log[H+]

## Slide 13: Acid Neutralizing Capacity (ANC or Alkalinity) Requirement
Al2(SO4)3 + 6H2O2Al(OH)3 + 6H+ + 3SO4-2
ANC is measured as mg/L of CaCO3
How much ANC is consumed by alum?
 | Alum | Calcium Carbonate
Molecular Formula | Al2(SO4)3*14H20 | CaCO3
Molecular mass | 600 g/mol | 100 g/mol
eq/mol | 6 | 2
Molecular mass/eq | 100 g/eq | 50 g/eq
Simple guide | 1 mg/L Alum consumes | 0.5 mg/L Calcium Carbonate ANC
This sets the maximum alum dose that can be used for low alkalinity waters
Notes: CUWFP has 140 mg/L calcium carbonate alkalinity. Therefore never have a problem with pH dropping too far with the addition of alum.
What do you do if the water ANC is too low? Add base OR switch to a less acidic coagulant.

## Slide 14: Polyaluminum Chloride (PACl)
Slowly titrated with a base (in the chemical plant) to produce a meta-stable and soluble polymeric aluminum (partially neutralized)
Consumes less alkalinity (ANC), it is less acidic.
Aluminum mass fraction is higher than in alum (no 14.3 H2O) so the mass of PACl required is less than for alum (0.4-10 mg/L as Al)
Notes: What is the chemical formula of PACl?

## Slide 15: PACl Formula and Basicity [Aln(OH)mCl3n−m] x
Basicity: Ratio of hydroxyl equivalents to aluminum equivalents
  Basicity of 1 would mean that it does not produce any protons when it dissolves in water
  0 means it produces 3 protons per Al (like alum)
The lowest basicity commercial PACls are about 10%
Most PACls are in the medium to high basicity range (50-70%)
Highest stable basicity (83%) is aluminum chlorohydrate (ACH) – would be useful for treating water with very low ANC
http://www.geosc.com/products/polyaluminum-chloride-(pac)
Notes: http://wioa.org.au/conference_papers/2001/pdf/paper6.pdf

## Slide 16: Sticky nanoparticles?
Effective flocculation only occurs when the coagulant is in the solid phase
  Thus NaOH and Ca(OH) 2 are not effective coagulants because they are soluble at neutral pH
Al(OH)3 likes to stick to itself and to other surfaces
Why is the solid phase Al(OH)3 and Al13O4(OH)24 7+ sticky? (Perhaps because it is more polar than water)

## Slide 17: Seeking favorable interactions between particles
We add a sticky insoluble coagulant that forms nanoparticles
We design reactor geometry and flow regimes to create interactions between
  Nanoparticles of coagulant precipitate
  Dissolved organic molecules
  Inorganic particles (like clay)
  Organic particles (including pathogens)

## Slide 18: Human hair is 50 mm in diameter
clay
bacterial cell
Coagulant nanoparticle

## Slide 19: Sizes of a few particles
7000 nm, 7 mm, 0.007 mm
90 nm, 0.09 mm
clay
Nanoparticle of coagulant
bacteria
1000 nm, 1 mm, 0.001 mm
50 nm, 0.05 mm
Natural organic matter

## Slide 20: How much coagulant should we add?
Our hypothesis:
When one clay platelet contacts another clay platelet, they will stick together if and only if there is a clean coagulant nanoparticle surface at the point of contact
We expect some aggregation to occur even with very low coagulant dosages
clay

## Slide 21: Evolving hypotheses
 | Previous Hypotheses | Previous predictions (proven incorrect) | Recent Hypotheses | Recent observed predictions
Particle attachment | Van der Waal forces | Coagulant won’t self aggregate because it is positively charged | Stronger noncovalent bonds or perhaps even covalent bonds | Fluid forces applied during flocculation consistent with stronger bonds
Role of coagulant | Neutralize the negative surface charge of particles | Flocculation will completely fail if surfaces become positively charged | Provide a sparse coating of coagulant nanoparticles on all particle surfaces | Particles attach over a wide range of coagulant dose
Particle collisions | Collisions between both similar and different sizes of particles occur | Primary particle concentration after flocculation should decrease when incoming primary particle concentration increases | Only similarly sized particles can collide | Primary particle concentration after flocculation is not significantly influenced by the incoming particle concentration
Notes: This is a field where progress has been very slow over the past century. A key factor is that new insights required a combination of fluid dynamics and chemistry

## Slide 22: Primary particle can not collide with a large floc in uniform shear* (edge of knowledge alert)
Thickness of viscous boundary layer, d, scales with floc diameter
Only similar sized particles can extend through each other’s viscous boundary layer.
Notes: I haven’t been able to find literature that demonstrates this effect.
Likely that the water contained within a floc simply rotates with the floc and that no new water enters the floc in a shear flow.

## Slide 23: Similar sized particles can collide in a shear flow

## Slide 24: Primary Particle collisions slow to a crawl when the primary particles are far apart
We need another strategy to capture particles including pathogens like Cryptosporidium
Notes: This insight is key. Otherwise highly turbid water would be predicted to produce super clean settled water!

## Slide 25: In shear flow only particles of similar size are able to collide
Higher turbidity raw water doesn’t produce cleaner water!
At the end of the flocculator the concentration of primary particles that haven’t flocculated is small and each collision takes a long time (rate limiting step)
The slow final stage of flocculation determines the final concentration of primary particles
A Hydrodynamic and surface coverage model capable of predicting settled effluent turbidity subsequent to hydraulic flocculation WH Pennock, ML Weber-Shirk, LW Lion
Environmental Engineering Science 35 (12), 1273-1285 (2018)
Notes: The final concentration of primary particles is independent of the raw water turbidity

## Slide 26: Wait! How do the coagulant nanoparticles get to the clay?
Molecular diffusion transports particles that are smaller than about 1 mm
Shear transports new fluid past the clay particles and molecular diffusion transports the nanoparticles through the viscous boundary layer!
Nanoparticles can diffuse through the boundary layer to the clay!
Notes: Coagulant nanoparticles are far smaller than the clay particles they attach to. So how are they transported to make the connection???

## Slide 27: Preview: Flocculation, Floc Blanket, Sand Filtration
We are developing a unified theory of these three processes
In each process we are attempting to capture particles that are dominated by viscous forces
Prior to the AguaClara flocculation model none of these processes had physics-based equations describing particle removal efficiency during normal operation
There is still a LOT of work to be done here to understand how these processes work and hence how to optimize the design of drinking water treatment plants

## Slide 28: Preview: Core idea for 3 water treatment processes
In laminar flow only similarly sized particles can collide
In floc blankets small particles flow through large flocs (stabilize by gravity) where they can collide with small particles
We hypothesize that sand filters work by capturing large flocs that then capture small particles! (the small particles flow through the captured flocs)
Notes: How do we know charge neutralization doesn’t explain flocculation
Floc aggregation begins even with very small dosages of coagulant long before the surface charge is neutralized
No transition in flocculation performance as the coagulant dose is gradually varied over a very wide range
No evidence of charge reversal causing deterioration in performance
A single physics-based model describes the full range of flocculation from low to high coagulant dosages
Coagulant nanoparticles are so large that they easily extend through the double layer and hence can directly bridge between two negatively charged particles
No one has been able to develop equations describing the role of charge neutralization
Confusion in the literature about whether WTPs use charge neutralization or sweep floc. No quantification of how you would know which hypothesized mechanism is operative

## Slide 29: Coming up
How fast do flocs form?
What controls the rate of collisions between particles?
What do the resulting flocs look like?
How does this influence how we design the reactors to build the flocs (flocculators)?