## Slide 1: Inlet and Outlet Manifolds and Plant Hydraulics
Using direct fluid feedback rather than indirect computer feedback to control flows
In which Changes in Kinetic Energy BECOMES SIGNIFICANT
(Thanks to A.A. Milne)

## Slide 2: Nomenclature: a start
Symbol | Description | Sub | 
Q | Flow | P | Port
A | Area | M | Manifold
 | Piezometric head | D | Diffuser
hL | Total Head Loss | e | expansion
HGL | Hydraulic Grade Line | 1 | Short path
EGL | Energy Grade Line | n | Long path
Cp | Pressure Coefficient (includes shear and expansion effects) |  | 
Pvc | Area of the vena contracta divided by the orifice area = 0.62 |  | 
D | Diameter |  | 
P | Dimensionless ratio |  | 
n | Number of ports |  | 
p | Pressure at the centroid of a control surface |  | 
 | Average velocity across a control surface |  | 

## Slide 3: Places we’d like Equal Flow Distribution
Sedimentation
  between sed tank bays
  between diffusers into sed tank
  between plate settlers
Filtration
  between filters
  Between filter layers
Notes: We currently use flow restrictions in the effluent launder to divide the flow between the sedimentation tanks.

## Slide 4
How does flow divide between layers?
Outlet box
Total filter head loss
Inlet plumbing head loss

## Slide 5: Sed Flow distribution
Inlet channel
Settled water outlet channel
Flocculated water to waste
Pipe stubs to block sed tank inlet manifolds
Weir that controls water level in sed tank (and flocculator)
Sensor access to floc hopper
Which sed tank will have the highest flow?
How could you reduce the difference in flows?
Notes: #6 will have the highest flow rate if inlet channel has a constant cross sectional area.

## Slide 6: Sedimentation tank controls
Entrance from the flocculator
Weir that maintains the water level in the flocculator when flocculating to waste
Wall between inlet and outlet channels
Exit to the filters
Exit weir that maintains the water level in the sedimentation tank (and flocculator)
Drain for flocculated water

## Slide 7: How can we make water split equally between several paths in a manifold?
Draw a manifold with ports that you think would give unequal flow. Orifices diameters are uniform.
Draw a manifold with ports that you think would give equal flow
What do you think is important? (pressure, elevation, kinetic energy)
n-1
2
n
1
cs1
csn
Inlet manifold
Notes: Vertical manifold or manifold at a slant?
Draw slanted pipe in a lake and discuss what causes water to flow in a pipe
Change in pressure or elevation or energy

## Slide 8: 4 strategies
Make the paths identical (try this first!)
Add custom head loss to each path (complicated!)
Increase identical head loss in all paths to make differences insignificant
  Sed inlet manifold diffuser pipes have high exit velocities
  Sed effluent manifold uses orifice head loss
Reduce head loss and pressure recovery that cause differences in piezometric head
  Use large diameter pipes for manifolds
Rule of thumb - exit and entrance velocities must be greater than manifold velocity!

## Slide 9: Piezometric head
Z=0
What is the piezometric head
in the tank?
In the pipe (no flow)?
In the manifold (with flow)
1
H
n
1
Piezometric head in an outlet manifold increases in direction of flow!
Neglect head loss
What sets H?
What sets change in piezometric head?
Notes: Fluid goes from high piezometric head to low piezometric head (for ports exiting normal to the flow)
Draw piezometers on

## Slide 10: Flow distribution between ports in an inlet manifold
Which port is going to get the most flow?
There is a very gradual flow expansion!
The water is being stopped by pressure on the end cap
Where is the manifold pressure highest?
n-1
2
n
1
cs1
csn
Inlet manifold
Notes: Draw manifold in lake picture
Define Pi.Q= Qp1/Qpn
Define H average (=vjet^2/2g) and DH (vpipe^2/2g) showing manometers
Note that shape of inlet (pitot tube) matters
DH proportional to 1/A^2 (from orifice eq)
How do you get Pi.Q = 1?
H average > DH
Ajet<Apipe

## Slide 11: Change in piezometric head from port 1 to port n (inlet manifold)
For short (fL/d <<1), straight (K=0) inlet manifolds the change in piezometric head is equal to the initial velocity head
The same for outlet manifolds except piezometric head decreases in the direction of flow
n-1
2
n
1
cs1
csn
Inlet manifold

## Slide 12: Change in piezometric head from port 1 to port n (outlet manifold)
For short (fL/d <<1), straight (K=0) outlet manifolds the change in piezometric head is equal to the negative final velocity head
2
n-1
1
n
csn
cs1
Inlet manifold

## Slide 13: Flow Division Analysis for Inlet Manifold (with orifice outlets)
Total difference between paths 1 and n
To simplify analysis we assume equal piezometric head error on both sides of the mean piezometric head (first order linearity approximation).
Port one has mean piezometric head – ½ delta piezometric head
Flow ratio is less than one
Last port has higher flow
We can achieve uniform flow by increasing
Engineering basis of design
Notes: Change in piezometric head is the same for both routes!
The loss coefficient is different and that means that the flows will be different too.
This is missing the effect of pressure recovery
Need a method to specify

## Slide 14: Solve for the maximum permissible change in piezometric head
Solve for
This is change in piezometric head in the manifold as a function of port flow uniformity and average piezometric head across the ports.

## Slide 15: Relationship between port contracted velocity and manifold velocity
If head loss in the manifold is small, then we have
Port flow uniformity equation
Piezometric head in the manifold (energy equation)
is the contracted port velocity
Pressure recovery
causes
differences in port flow
The average manifold piezometric head sets the average port velocity

## Slide 16: Manifold velocity
No head loss in series
With helpful head loss in series
Pressure recovery =

## Slide 17: Plot port velocity over manifold velocity as a function of
Total contracted port area must be smaller than pipe (manifold) area to get reasonable flow distribution

## Slide 18: Filter Inlet Channel Design
Channel provides water to all of the filters
Water exits the channel by flowing over the top of sharp crested weirs to enter the filter inlet boxes
Small changes in water elevation in the channel will cause significant changes in flow rate to the filters

## Slide 19: Manifold Channel
Looking toward channel from filter inlet boxes
Water in filter inlet
Water in channel
Filter 1
Filter n/2
Filter n

## Slide 20: Open channel side exit weir flow distribution
Define the flow ratio
Solve for the maximum manifold velocity
Alternative solution is slope the bottom of the channel (but this doesn’t solve the problem when some filters are off line)
Assumes 5 cm over the weirs

## Slide 21: Sed Tank as a Circuit: Flow Distribution Challenge
Inlet channel
Settled water outlet channel
Inlet manifold
Diffuser exit loss
Launder orifice loss
Floc blanket and plate settlers
Effluent manifold (Launder)
Piezometric head change from
Flow deceleration and head loss
Battery creates 5 to 10 cm of potential energy to drive the flow
Piezometric head change from flow acceleration and head loss
Launder exit losses
Flow distribution thru parallel paths is a major hydraulic design challenge
Notes: We will cover this in manifold hydraulics if we have time. Which resistance is good and improves flow distribution? Which resistance makes flow distribution poor?
Improve by increasing losses in diffusers and in orifices

## Slide 22: Manifold flow distribution Including major head loss
We will derive equations in terms of Hydraulic Grade Line (HGL) because piezometric head controls the port flow
Port flow
  based on _______ equation
Piezometric head change (Y) across port
  flow expansion
Piezometric head change (Y) between ports
  Darcy-Weisbach and Swamee-Jain
orifice
In manifold

## Slide 23: Inlet Manifold
1
n-1
2
n
EGL
HGL
Major head loss
Pressure recovery
Change in piezometric head from expansion pressure recovery across one port (flow expansion)
Notes: Which port has the highest flow

## Slide 24: What is as a function of n? (sum of the change in piezometric head from expansions)
Approaches for large n
_______________ is recovered for very gradual expansion.
All kinetic energy
Now sum across all ports

## Slide 25: Outlet Manifold (Launder)
1
n-1
2
n
All of the changes at the ports sum to
Flow contractions, thus no significant minor loss!
EGL
HGL

## Slide 26: Head Loss in a Manifold (same for inlet or outlet)
Define manifold length as
Head loss in a manifold is __ of the head loss with constant Q.
1/3

## Slide 27: Change in Piezometric Head in an Outlet Manifold
Note: We have factored out the friction factor knowing that and thus f is not constant
Total change in piezometric head

## Slide 28: Change in Piezometric Head in an Inlet Manifold
This equation gives the difference in piezometric head between the first port and the last port. Since the two terms have opposite signs the maximum difference could be at an intermediate port. We need to determine if one of these terms dominates to see if the maximum difference really is between the first and last ports.

## Slide 29: Conclusions
Manifolds are complicated (and important)!
Manifold head loss is 1/3 the head loss in a pipe
Difference in piezometric head drives the flow through the ports
Manifold kinetic energy is converted to pressure increase
Following slides develop equations for detailed design of manifolds (reference for your future careers!)

## Slide 30: Solution Path
The length of the manifold will be determined by the plant geometry
The spacing of the ports will be set by other constraints
We need to determine the diameter of the manifold and the diameter of the ports

## Slide 31: Launder: Traditional Design Guidelines
Recommended port velocity is 0.46 to 0.76 m/s (Water Treatment Plant Design 4th edition page 7.28)
  The corresponding head loss is 3 to 8 cm through the orifices
  How do you design the diameter of the launder? (coming up…)
  Would this work if head loss through the manifold were an additional 10 cm? _____
NO!
Notes: Water Treatment Plant Design 4th edition page 7.28

## Slide 32: Design Constraints
For sed tank Inlet Manifold the port velocities and the manifold diameter are set by the _____________________________________
For the outlet manifold that takes clear water from the top of the sed tank bays the goal will be to keep head loss low and greater than construction errors in level of weir (we aim for about 5 cm)
Diffuser jet velocities

## Slide 33: Why is the launder diameter so large?
(50L/s /9) launder of 6 inches
The head loss in the launder is small and it would be tempting to use a smaller pipe
Why is such a large pipe necessary?______________
Why do we even need a launder pipe? ___________________________________________ ___________
What is the max velocity above the plate settlers given a 1 m wide tank, 25 cm of water above the plates, a single launder? __________
Equal orifice flow
For uniform flow distribution between (and within) plate settlers
2 mm/s
Notes: I take the last question as a real question. Do we actually need launders? Would it be better to lay a perforated cloth on top of the plate settlers to help get uniform flow distribution between plates and then use a simple orifice in the channel wall to create 5 cm of head loss to force flow between bays to be equal?

## Slide 34: What is the horizontal velocity above the plate settlers without a launder?
This velocity is very large compared with the head loss through the plate settlers (about 1 mm) and thus elimination of the launder would result in preferential flow through the plate settlers closest to the exit

## Slide 35: Approach to Find Port Diameter
Calculate the head loss in the manifold
Subtract 50% of that head loss from the target head loss (5 cm) to estimate the port head loss
Calculate the port diameter directly using the orifice equation

## Slide 36: Hydraulic Conclusions
The water level in the flocculator and sedimentor is set by the settled water weir
The most significant head loss in the sedimentation tank is the orifices in the effluent manifold
The entrance tank water level is significantly higher than the flocculator due to head loss in the LFOM
The stock tanks have to be even higher to be able to flow by gravity thru the chemical doser and into the entrance tank.