## Slide 1: AguaClara Surface Water Treatment
Screening, grit removal, flow measurement
Hydraulic
Flocculation
Plate Settlers
Stacked Rapid
Sand Filtration
Storage
Distribution
Raw water
Coagulant
Cl2
sludge
sludge
Backwash water
Floc Filter
Floc Hopper
Backwash recycle proposed
Clarifier

## Slide 2: Components of a Clarifier
Plate Settlers
Floc filter
Floc hopper
Inlet manifold
Outlet manifold
Notes: Why is it called a clarifier?
How does flocculated water get into the clarifier?
How do flocs get from the floc filter into the floc hopper?

## Slide 3: How much space (plan view area) for 1 L/s?
Q=VA! - What is the upflow velocity through the floc filter?
A = Q/V = 0.001 m3/s/(0.001 m/s)

## Slide 4: Four sizes/types of Floc
New flocs in the floc filter
Full flocs in the floc filter
Primary particles and flocs too small to be captured by the plate settlers
Flocs that settle fast enough to be captured by the plate settlers but not fast enough to stay in the floc filter

## Slide 5: Which of these ISN’T true?
"full" flocs are removed via the floc hopper
primary particles settle out
non-full flocs are removed via the floc hopper
primary particle are captured/filtered by flocs
flocs with terminal velocities lower than the upflow velocity in the clarifier are captured by the plate settlers and avalanche to form flocs that stay in the floc filter

## Slide 6: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Inlet (from flocculator)
Floc Hopper
Floc Filter
Effluent manifold
Plate Settlers
Notes: Story
Big green flocs from flocculator form blue floc filters in the plate settler
Red flocs

## Slide 7: Which of these ISN’T true? (break out rooms for 3 minutes – then vote)
"full" flocs are removed via the floc hopper
primary particles settle out
non-full flocs are removed via the floc hopper
primary particle are captured/filtered by flocs
flocs with terminal velocities lower than the upflow velocity in the clarifier are captured by the plate settlers and avalanche to form flocs that stay in the floc filter

## Slide 8: Primary particle sedimentation
Primary particles don't settle out because they are in suspension right?
  A fast flow river can have sand and even gravel in suspension!
Will primary particles ever settle out in a clarifier?
Why do we flocculate the water?
  It is fun
  We wanted to be able to see the dirt
  To increase the sedimentation velocity
Notes: Won’t settle out if the water is flowing!

## Slide 9: Quiz 31
Explain the difference between flocculation and clarification
How large do flocs get?

## Slide 10: Jet engines create a round fluid jet to generate thrust
By Shelley Gill - 123232730, Public Domain, https://commons.wikimedia.org/w/index.php?curid=12358905

## Slide 11: What is a fluid jet?

## Slide 12: Floc colors
Can you see the green flocs? Can the plant operators see green flocs?
The colors that I gave to the flocs in the presentation are just to make it easy to talk about them. They aren’t actually those colors. Flocs vary in color from white to brown (from what I’ve seen)

## Slide 13: Floc Filter, Plate Settler, Floc Hopper
 | Terminal Velocity | 
 |  | 2
 |  | 2
 |  | 2
 |  | >2
Inlet (from flocculator)
Floc Hopper
Floc Filter
Effluent manifold
Plate Settlers
Notes: What is acting like a filter inside the clarifier?
What controls the supply of big blue flocs in the floc filter?
Under what conditions would there be more new big blue flocs entering the floc filter?
What are big blue flocs made from?
Propose 2 methods to increase the supply of big blue flocs.

## Slide 14: Prepare to type the answers to questions 4 and 5 in the chat
What is acting like a filter inside the clarifier?
What controls the supply of big blue flocs in the floc filter?
Under what conditions would there be more new big blue flocs entering the floc filter?
What are big blue flocs made from?
See if you can come up with 2 methods to increase the supply of big blue flocs.